## B
Releases to Air
PPC Reporting - Nox and CO
Operational Summary for dates 1 January 2023 to 31 December 2023
| Operator: |  | National Gas |  |  | Site Location: | Felindre
Compressor Station
| Permit/Variation number: |  |  | RP3232LD |  | Release Point: | A1
Measurement frequency: As given in table S4.1 and shown below
When operational hours in any year are less than or equal to 2,200 hours:
To be reported every 2 years
When operational hours in any year are greater than 2,200 hours:
To be reported every year or every 4,380 operational hours, whichever is sooner
Following any changes to process equipment, configurations or operating practises that may affect the accuracy of the data generated by the Predictive Monitoring System
|  |  | Time & date of sampling | 10:06 - 13:11 on 21/02/23
Pollutant |  |  | ELV mg/m3 | Measure value mg/m3 | Sampling method | Unit Load or %MCR |  | % Deviation from PEMS
NOx |  |  | 75 | 21.8454 | Extractive | 79.2066 |  | 29.3691
|  |  |  | 18.9555 |  | 80.0764 |  | 13.2195
|  |  |  | 18.039 |  | 83.539 |  | 12.2365
|  |  |  | 18.0619 |  | 85.4151 |  | 15.234
|  |  |  | 18.7806 |  | 89.5198 |  | 26.2264
|  |  |  | 17.2094 |  | 93.6396 |  | 21.3335
|  |  |  | 16.4002 |  | 98.244 |  | 23.0075
|  |  |  | 18.8939 |  | 100.0175 |  | 46.6741
|  |  |  | 28.3846 |  | 104.4719 |  | 133.0615
CO |  |  | 100 | 10.0019 | Extractive | 79.2066 |  | 131.4584
|  |  |  | 10.2598 |  | 80.0764 |  | 132.2086
|  |  |  | 7.1304 |  | 83.539 |  | 51.5173
|  |  |  | 6.5641 |  | 85.4151 |  | 37.4719
|  |  |  | 6.6912 |  | 89.5198 |  | 44.493
|  |  |  | 5.7155 |  | 93.6396 |  | 32.0089
|  |  |  | 7.9255 |  | 98.244 |  | 68.9215
|  |  |  | 7.5772 |  | 100.0175 |  | 44.3575
|  |  |  | 7.1998 |  | 104.4719 |  | 16.2447
Operational hours since last submissions of discontinuous monitoring: | [6 empty] | 1963
|  |  | Signed on behalf of the operator |  | M Secomb
| Date |  | 2023-04-21
Form: Air 3 - PPC discontinuous (NOx & CO)
Date of Form: 22/11/06
|  |  | Max MCR | 42 | pems deviation |  |  |  | measured values
|  |  | 33.2668 |  | 29.3691 | 131.4584 |  |  | 21.8454 | 10.0019
|  |  | 33.6321 |  | 13.2195 | 132.2086 |  |  | 18.9555 | 10.2598
|  |  | 35.0864 |  | 12.2365 | 51.5173 |  |  | 18.039 | 7.1304
|  |  | 35.8743 |  | 15.234 | 37.4719 |  |  | 18.0619 | 6.5641
|  |  | 37.5983 |  | 26.2264 | 44.493 |  |  | 18.7806 | 6.6912
|  |  | 39.3286 |  | 21.3335 | 32.0089 |  |  | 17.2094 | 5.7155
|  |  | 41.2625 |  | 23.0075 | 68.9215 |  |  | 16.4002 | 7.9255
|  |  | 42.0073 |  | 46.6741 | 44.3575 |  |  | 18.8939 | 7.5772
|  |  | 43.8782 |  | 133.0615 | 16.2447 |  |  | 28.3846 | 7.1998

## C
Releases to Air
PPC Reporting - Nox and CO
Operational Summary for dates 1 January 2023 to 31 December 2023
| Operator: |  | National Gas |  |  | Site Location: | Felindre
Compressor Station
| Permit/Variation number: |  |  | RP3232LD |  | Release Point: | A2
Measurement frequency: As given in table S4.1 and shown below
When operational hours in any year are less than or equal to 2,200 hours:
To be reported every 2 years
When operational hours in any year are greater than 2,200 hours:
To be reported every year or every 4,380 operational hours, whichever is sooner
Following any changes to process equipment, configurations or operating practises that may affect the accuracy of the data generated by the Predictive Monitoring System
|  |  | Time & date of sampling | 16:02 - 16:48 on 21/02/23
Pollutant |  |  | ELV mg/m3 | Measure value mg/m3 | Sampling method | Unit Load or %MCR |  | % Deviation from PEMS
NOx |  |  | 75 | 24.3029 | Extractive | 77.0148 |  | 6.5033
|  |  |  | 25.0685 |  | 79.7251 |  | 4.8564
|  |  |  | 25.0798 |  | 82.027 |  | 1.199
|  |  |  | 25.2651 |  | 84.9986 |  | -2.6348
|  |  |  | 27.0138 |  | 88.5295 |  | -1.0945
|  |  |  | 27.7115 |  | 92.428 |  | -4.0457
|  |  |  | 27.4337 |  | 96.4164 |  | -9.8388
|  |  |  | 27.6116 |  | 99.5977 |  | -12.8817
|  |  |  | 42.1412 |  | 102.3049 |  | 28.8486
CO |  |  | 100 | 1.0693 | Extractive | 77.0148 |  | -65.3035
|  |  |  | 1.055 |  | 79.7251 |  | -31.0773
|  |  |  | 0.83972 |  | 82.027 |  | -41.5755
|  |  |  | 1.0879 |  | 84.9986 |  | -20.9039
|  |  |  | 0.72436 |  | 88.5295 |  | -44.4108
|  |  |  | 0.84077 |  | 92.428 |  | -31.0808
|  |  |  | 0.47395 |  | 96.4164 |  | -58.3465
|  |  |  | 0.49772 |  | 99.5977 |  | -53.512
|  |  |  | 0.70224 |  | 102.3049 |  | -30.9484
Operational hours since last submissions of discontinuous monitoring: | [6 empty] | 1355
|  |  | Signed on behalf of the operator |  | M Secomb
| Date |  | 2023-04-21
Form: Air 3 - PPC discontinuous (NOx & CO)
Date of Form: 22/11/06
|  |  | Max MCR | 42 | pems deviation |  |  |  | measured values
|  |  | 32.3462 |  | 6.5033 | -65.3035 |  |  | 24.3029 | 1.0693
|  |  | 33.4846 |  | 4.8564 | -31.0773 |  |  | 25.0685 | 1.055
|  |  | 34.4514 |  | 1.199 | -41.5755 |  |  | 25.0798 | 0.83972
|  |  | 35.6994 |  | -2.6348 | -20.9039 |  |  | 25.2651 | 1.0879
|  |  | 37.1824 |  | -1.0945 | -44.4108 |  |  | 27.0138 | 0.72436
|  |  | 38.8198 |  | -4.0457 | -31.0808 |  |  | 27.7115 | 0.84077
|  |  | 40.4949 |  | -9.8388 | -58.3465 |  |  | 27.4337 | 0.47395
|  |  | 41.831 |  | -12.8817 | -53.512 |  |  | 27.6116 | 0.49772
|  |  | 42.9681 |  | 28.8486 | -30.9484 |  |  | 42.1412 | 0.70224