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This page outlines the information that the Operator must provide to satisfy conditions 5.1.1 and 5.1.2 of this Permit. 
Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.
If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the PPC Regulations.
Part A 
	Permit Number
	BU8002 

	Name of Operator
	Dunbia Cross Hands

	Location of Installation
	Cross Hands Food Park, Llanelli, Carmarthenshire SA14 6RF

	Location of the emission
	W5 

	Time and date of the emission
	30/06/2023 at 09:00  



	Substance(s) emitted
	Media
	Best estimate of the quantity or the rate of emission
	Time during which the emission took place

	Ammoniacal Nitrogen
	Surface water W5
	0.7mg/l – Limit 0.25mg/L

	09:00



	Measures taken, or intended to be taken, to stop the emission
	Following receipt of this result an investigation was completed. No tangible causes for the exceedance were identified.  It is believed that the limit of 0.25mg/L is too low to achieve.
However, the sample was taken just at the start of the flow of rainfall, thus not giving the drainage channel an opportunity to flush leaves / algae that has built up over the last couple of months.  
As a site we continue to monitor activity to establish potential causes. 




Part B
	Any more accurate information on the matters for notification under Part A.
	As above.

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	As above. 

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment or harm which has been or may be caused by the emission
	As above.

	The dates of any unauthorised emissions from the installation in the preceding 24 months.
	14/01/21, 21/08/21, 30/11/21, 29/12/21, 27/05/22, 09/09/22, 30/12/22, 30/06/23 



	Name*
	Lewis Elsey 

	Post
	HSE Officer 

	Signature
	L. Elsey 

	Date
	10/06/2023


* authorised to sign on behalf of Dunbia (UK) Ltd

