Aberthaw Power Station Improvement Condition 41: Conversion to High Volatile Matter Coals - Commissioning Report May 2019

Copyright © 2019 RWE Generation UK plc

All pre-existing rights reserved.

This document is supplied on and subject to 
the terms and conditions of the Contractual Agreement relating to this work, under which 
this document has been supplied, in particular:

Confidentiality

This document is not confidential.

Liability

In preparation of this document RWE Generation UK plc has made reasonable efforts to ensure that the content is accurate, up to date and complete for the purpose for which it was contracted. RWE Generation UK plc makes no warranty as to the accuracy or completeness of material supplied by the client or their agent. Other than any liability on RWE Generation UK plc detailed in the contracts between the parties for this work RWE Generation UK plc shall have no liability for any loss, damage, injury, claim, expense, cost or other consequence arising as a result of use or reliance upon any information contained in or omitted from this document. 

Any persons intending to use this document should satisfy themselves as to its applicability for their intended purpose.

The user of this document has the obligation 
to employ safe working practices for any activities referred to and to adopt specific practices appropriate to local conditions.

# Aberthaw Power Station

# Improvement Condition 41: Conversion to High Volatile Matter Coals - Commissioning Report

| Prepared by: |  |
| --- | --- |
| Richard Powell |  |

| Reviewed by: | Authorised by: |
| --- | --- |

Table of contents

1	Introduction	4

2	Commissioning Completion Dates	5

3	Noise Levels associated with Commissioning Activities and Routine Start Up and Operation	5

4	Fugitive dust emissions associated with coal stocking and handling	6

5	Ash quality (and identification of the need for PFA landfill design review)	6

6	Carbon in Ash CiA	6

7	Tube Failure Rates	6

8	Start up, Shut Down Thresholds and Boiler Stability	6

9	Slagging	6

10	Thermal Performance	7

11	CEMs performance	7

12	Electrostatic Precipitator ESP Performance	7

13	FGD Performance	9

14	NOx emissions	9

15	BAT ELVs for NOx	10

16	CO Emissions	11

Appendix A.	Engineering Test Plan	12

Introduction

This document is written in response to Improvement Condition 41 of the Environmental Permit, which asks for the following information to be submitted after 6 months of operations:

Following the commissioning of Units 7, 8 and 9 and a period of 6 months operation on HVMC, the Operator shall submit a written post-commissioning report to Natural Resources Wales for approval. The report shall confirm the commissioning completion date for each unit conversion to bituminous coal firing. The report shall also state the emission reductions achieved and relevant performance parameters under the full range of operating scenarios, including, but not limited to:

• noise levels associated with commissioning activities and routine start up and operation

• fugitive dust emissions associated with coal stocking and handling

• ash quality (and identification of the need for PFA landfill design review)

• carbon in ash levels

• tube failure rates

• start up, shut down thresholds and boiler stability

• slagging

• thermal performance

• CEMs performance

• electrostatic precipitator performance

• FGD performance

• NOx emissions, including NO:NO2 ratio

• CO emissions

The report shall include a justification of the Best Available Techniques Emission Limit Values (BAT ELVs) to be adopted upon full optimisation of all units, including a date by which the BAT ELVs will be achieved.

An interim report was submitted to NRW at the end of May 2018 in response to Improvement Condition 41 in the Stations Environmental Permit. The report was interim in nature due to the limited amount of data available post High Volatile Matter VM Coal commissioning at that time and therefore it was agreed that an update report would be submitted at end May 2019. The second report was intended to include more extensive data in order to evaluate any changes in operation as a result of the move to burn higher volatile coal, however as can be seen due to limited running there remains a small data set in order to draw conclusions.

Commissioning Completion Dates

A summary of the key commissioning dates, fuel diet during operational periods and the operational hours is provided below:

| Activity | Unit 7 | Unit 8 | Unit 9 |
| --- | --- | --- | --- |
| Return to Service with Operation on Low Volatile Coal - Control System Tuning and Defect identification | 25/09/17 - 14/01/18 | 30/10/17 - 15/11/17 | 29/11/17 - 04/12/17 |
| Transition to Neat HVMC on individual Mills | n/a | 16/11/17 - 31/11/17 | 05/12/17 - 15/12/17 Only two of six mills transitioned. |
| All Mills on Neat HVMC coal | n/a | 01/12/17 - 15/12/17 | n/a |
| Transition to 50:50 HVMC and LVMC blend on individual Mills | 15/01/18 - 19/01/18 | 16/12/17 - 25/01/18 | 16/12/17 - 25/01/18 |
| Operation on 50:50 HVMC:LVMC blend and investigation of higher blend ratios | 19/01/18 - 27/03/18 | 26/01/18 - 27/03/18 | 26/01/18 - 27/03/18 |
| Operation on 100% HVMC | 24/09/18 - present | 11/10/18 - present | 12/09/18 - present |

|  | Unit 7 (hours) | Unit 8 (hours) | Unit 9 (hours) |
| --- | --- | --- | --- |
| Operational Hours above SEL from Sept 2017 to April 2018 | 257 | 280 | 273 |
| Operational Hours above SEL from Sept 2018 to April 2019 | 358 | 303 | 454 |

Noise Levels associated with Commissioning Activities and Routine Start Up and Operation

The table below shows average hourly noise data for the locations listed during January to April before and after the conversion. The data relates to periods when at least one of Aberthaw’s generating units was generating more than 50MW. This data has not been filtered for weather conditions. The data shows that there has been no appreciable effect on the general noise emission from the Power Station as a result of the Hi Volatile Coal transition.

| Location | 2016 Jan – Apr Pre high VM coal | 2018 Jan – Apr Post high VM coal | 2019 Jan – Apr Post high VM coal |
| --- | --- | --- | --- |
| Limpet Bay | 56.4 | 48.7 | 55.3 |
| Aberthaw Stack | 63.9 | 58.7 | 60.0 |
| Gilestone | 49.5 | 49.0 | 47.1 |

Fugitive dust emissions associated with coal stocking and handling

There has been no fugitive dust emission issues associated with stocking or handling of the high volatile coal.

Ash quality (and identification of the need for PFA landfill design review)

A detailed laboratory analysis of Aberthaw’s PFA was carried out in December 2018 and the results for particle size, particle density and shear strength are all consistent with historic results. This suggests that there is no requirement to review the design of the Quarry Ash Landfill Site.

Carbon in Ash CiA

From the small amount of data collected so far; the carbon in ash levels when firing high VM coal are lower than compared to firing on the historic low volatile coals. The data collected in Q4 2018 and Q1 2019 show average CiA levels of between 2 – 5%, with historic levels being >10%.

Tube Failure Rates

There has been no perceivable increase in boiler tube failure rates post high VM coal conversion.

Start up, Shut Down Thresholds and Boiler Stability

The Start-up / Shut Down ‘SUSD’ threshold was reduced to 280MW(sent out) for Unit 9 in December 2018, a Plant Modification Procedure was followed to fully assess this change prior to implementation. The reason for the change was to increase commercial flexibility and was enabled due to the plant modifications carried out as part of the Unit 9 Low NOx Boiler Project. The SUSD thresholds are unchanged at 380MW(sent out)  for units 8 and 9.

There have been no issues with boiler stability as a result of the change to high VM coal over the three units or due to the reduced SUSD on U9.

Slagging

Following U9 Low NOx conversion in 2015, there was an increase in slag build up, which has been reduced over the years through tuning of air flows. Further to this, following NOx reduction modifications to U7 and U8, the nature of slag build up again increased slightly in line with expectations due to the more reducing conditions in the furnace. Since the Hi VM conversion, operation has been more intermittent, which lends itself to reducing slag formation through repeated expansion and contraction of the tubes. As such, the slag formation appears reduced since Hi VM conversion, as anticipated through the fuel change, but it is likely more dominated by operation regime. Slagging propensity is a consideration in the coal selection process.

Thermal Performance

Thermal efficiency has been reviewed before and after the conversion.  Although efficiency was lower in 2018/19 this is due to the large reduction in operational hours and an infrequent operational  pattern.  Therefore it is difficult to infer any effect from the change to high VM coal in 2018.  As reported previously the boiler final gas temperatures have not changed which indicates that the thermal performance of the boilers has not deteriorated.

As the efficiency figures are commercially confidential we have not included them in this report but these can be made available for inspection if appropriate.

CEMs performance

During the commissioning period CEMS were fully available. The instrumentation has functioned as normal and the subsequent full conversion to high VM coal  has had no impact on CEMS performance.

During the calendar year 2018 there were zero invalid reportable days which indicates that CEMS availability and functionality was good.

During the first quarter of 2019 the majority of the CEMS quality assurance testing was successfully completed which included QAL2 tests on Unit 7 & 9 and AST tests on Unit 8.

Electrostatic Precipitator ESP Performance

The charts below show the dust concentration in the flue gas exiting the ESP’s between January 2016 and March 2019. The data for Units 8 and 9 show that there has been no deterioration in dust concentration exiting the ESP’s during or after the high VM coal conversion. There was an increase on Unit 7 during Q1 2018 however there were identified plant malfunctions in Unit 7 ESP’s that can explain this and the dust levels have subsequently returned to historic levels once the malfunctions were rectified. Therefore, it is concluded that the conversion has not had a detrimental impact on ESP performance.

FGD Performance

The chart below shows the hourly average stack SO2 concentrations for the Station between January 2016 and March 2019. The trend shows that there has been no increase in SOx concentrations and hence deterioration in FGD performance due to high VM coal transition.

NOx emissions

The figure below shows the station’s actual hourly average NOx emission (i.e. not validated data) from the January 2018 until May 2019. As mentioned previously due to operational problems over the period Jan to March 2018 the station was not commissioned to operate on 100% high VM coal but instead utilised a blend of 50:50 low and high VM blend. During the period September 18 to March 2019 all units achieved operation on 100% high volatile coal but importantly did not achieve full load. Due to lack of opportunity because of low load factor it was not possible to carry out NOx optimisation on the units post high VM coal operation. A NOx optimisation test plan has been created (see appendix) and the intention is to fully optimise the units when the opportunity arises, however this is dependent on load factor/operational pattern.

Over the whole period inc commissioning on 50:50 blend and transition to 100% high VM coal, the average of the hourly NOx concentrations was 475 mg/Nm3.  However, due to the very low load factor for the station (~4% during 2018) there is very limited data available and is therefore not representative of the much wider range of operational conditions possible. In particular the Station did not achieve full load for the majority of the period Sept 18 – March 19

Taking all these factors into account NOx performance has been generally in line with expectations following the plant modifications. However as mentioned previously steady state at full load has not yet been achieved on 100% high VM coal and therefore the NOx performance over the full operating range of the units has not been evaluated against expected levels.

The QAL 2 testing carried out during Q1 2019 showed that the % split between NO and NO2 was as follows :

NO         NO2

Unit 7                    98.9        1.1

Unit 8                    99.5        0.5

Unit 9                    99.1        0.9

BAT ELVs for NOx

Given the limited running and lack of opportunity to optimise NOx performance we propose the current BAT ELVs remain in place until the end of the TNP. Thereafter the available data does not support a BAT  ELV which is  lower  than the IED requirements, particularly given  Aberthaw’s role as a peaking plant supporting security of supply.  Periods of generation may potentially be of a short duration and intermittent within the IED monthly averaging period.  In this context the BAT ELV needs to account for the inherent operational variability, as concentrations may be higher over shorter periods than if averaged over a full month of operation.  With this in mind examination of the data (Section 14) indicates that the IED emission limits represent BAT for the station in this context

CO Emissions

The following figure shows the stations hourly average CO emission in ppm (normalised to dry and 6% O2) between January 2018 and February 2019.  The measured levels are a reflection of the fact that due to the limited periods of operation, combustion optimisation was not practicable.

Engineering Test Plan

| Subject / Title: | Test Plan:- Aberthaw Power Station NOx Optimisation on High Volatile Matter Coal |
| --- | --- |
| Document ref: | TECH/TEF/3153/19 |
| Issue date: | 22nd May 2019 |
| Client: | Aberthaw Power Station |
| TS Group/Team | Fuels, Combustion & Emissions Technology (FCET) |

# Objective

The objective of this test is to determine the optimal NOx performance across the load range (Stable Export Limit to Maximum Export Limit) while operating on High Volatile Matter (HiVM) Coal. The performance of non-Low NOx Boiler (LNBo) (Units 7 and 8) and LNBo Units will be evaluated separately. Based on findings from these trials operational recommendations will be made to achieve low NOx emissions from all units.

# Trial Overview

NOx emissions are to be evaluated on Carbo One coal. In order to evaluate NOx emissions Mill and PF burner availability will need to be high and mill moisture is to be sufficiently low to allow for operation without oil support. The unit’s load will need to be held at full load for a period of approximately three hours in order to evaluate emissions at full load. Part load optimisation will be conducted during normal unit operation (no scheduled load drops to part load).

Carbon Monoxide emissions should also be monitored during the trial and maintained below 500ppm while optimising boiler firing.

# Test Plan

Requirements for the trial:-

Final Feedwater temperature ~240C

Carbo One High VM coal supplied to all mills on test unit

No Sootblowing during test

Stable load for testing

Details of the test plan are presented in the table below.

| Description | Timeline | Responsibility |
| --- | --- | --- |
| Day 1 | Optimisation of Non-LNBo Units (U7&8) at full load - MEL = SEL = 520MWso on Unit 7 or 8 for a period of 3 hours - Six Mills in-service - Reduce dynamic classifier speeds to 90rpm - Reduce number of PF fires to a minimum and reduce the number of centre fires in service - Adjust firing pattern to reduce NOx - Reduce excess air to a minimum while monitoring CO emissions | Operations |
|  | Optimisation of Non-LNBo Units (U7&8) at part load - Optimisation to be carried out when units are operating at less than full load - Five or Six Mills in-service - Reduce dynamic classifier speeds to 90rpm - Reduce number of PF fires to a minimum and reduce the number of centre fires in service - Adjust firing pattern to reduce NOx - Reduce excess air to a minimum while monitoring CO emissions | Operations /Performance |
| Day 2 | Optimisation of LNBo Unit (U9) at full load - MEL = SEL = 520MWso on Unit 7 or 8 for a period of 3 hours - Six Mills in-service - Reduce dynamic classifier speeds to 90rpm - Reduce number of PF fires to a minimum and reduce the number of centre fires in service - Adjust firing pattern to reduce NOx - Reduce excess air to a minimum while monitoring CO emissions | Operations / Performance |
|  | Optimisation of LNBo Unit (U7&8) at part load - Optimisation to be carried out when units are operating at less than full load - Five or Six Mills in-service - Reduce dynamic classifier speeds to 90rpm - Reduce number of PF fires to a minimum and reduce the number of centre fires in service - Adjust firing pattern to reduce NOx - Reduce excess air to a minimum while monitoring CO emissions | Operations /Performance |