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This page outlines the information that the Operator must provide to satisfy conditions 5.1.1 and 5.1.2 of this Permit. 
Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.
If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the PPC Regulations.
Part A 
	Permit Number
	BU8002 

	Name of Operator
	Dunbia Cross Hands

	Location of Installation
	Cross Hands Food Park, Llanelli, Carmarthenshire SA14 6RF

	Location of the emission
	W5 

	Time and date of the emission
	13/07/2023 at 09:00  



	Substance(s) emitted
	Media
	Best estimate of the quantity or the rate of emission
	Time during which the emission took place

	Ammoniacal Nitrogen
	Surface water W5
	0.3mg/l – Limit 0.25mg/L

	09:00

	Ph  	
	Surface water W5 
	9.6 – Limit 6-9 
	09.00



	Measures taken, or intended to be taken, to stop the emission
	Following receipt of this result an investigation was completed. 
It was identified that during the date the sample was obtained there was a considerable amount of jet washing of the pathways and building being carried out.
The area had not been jet washed for many years therefore there was a large build up of silt, moss and algae present.
The jet washing process would have resulted in some of the washdown entering the drainage channels that leads to the W5 sample point.
There was no chemical used in the washdown just high pressure water, however algae is high in alkali therefore contributing to the PH increase.
Going forward the washdown will be completed more frequently therefore the build up of algae will not be as much, in addition to this the larger sections removed during the process will be collected prior to entering the drainage system and disposed of.



Part B
	Any more accurate information on the matters for notification under Part A.
	As above.

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	As above. 

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment or harm which has been or may be caused by the emission
	As above.

	The dates of any unauthorised emissions from the installation in the preceding 24 months.
	14/01/21, 21/08/21, 30/11/21, 29/12/21, 27/05/22, 09/09/22, 30/12/22, 30/06/23, 13/07/23



	Name*
	Chris Dodd 

	Post
	HSE Manager 

	Signature
	C. Dodd 

	Date
	24/08/2023


* authorised to sign on behalf of Dunbia (UK) Ltd

