 RELEASES INTO CONTROLLED WATERS

Release Summary for Quarter 1                           Year 2023     Permit No. BL 4567


Operator Vale Europe Ltd.,


                 Location: Clydach SA6 5QR



	Parameter
	Release Point Number

	
	W1
	Cooling Water flows (at W1)
	W3
	W4
	W5
	W6
	W7
	W8
	W9

	
	Limits
	Results
	
	
	
	
	
	
	
	

	Maximum Flow

   m3/hour
	625
	185.83
	
	----

X
	50

X
	4.5

X
	11

X
	----

X
	3

X
	----

X

	Mean Flow

   m3/hour
	
	74.85
	
	
	
	
	
	
	
	

	Maximum Flow

   m3/day
	15000
	4460.00
	
	----

X
	600

X
	13

X
	270

X
	----

X
	15

X
	----

X

	Mean Flow

   m3/day
	
	1796.39
	
	
	
	
	
	
	
	

	 pH Maximum
	9.0
	7.90
	
	
	
	
	
	
	
	

	 pH Mean
	N
	7.48
	
	
	
	
	
	
	
	

	 pH Minimum
	6.0
	5.80
	
	
	
	
	
	
	
	

	Temperature °C
	+20
	14.92
	
	
	
	
	
	
	
	

	Temperature Canal Abstraction °C     *
	
	5.53
	
	
	
	
	
	
	
	

	Suspended Solids mg/l
	10.0
	1.757
	
	
	
	X
	X
	X
	
	

	Total Copper mg/l

(Cu)
	0.5
	0.055
	
	
	
	
	
	X
	
	

	Soluble Copper mg/l

(Cu)
	0.5
	0.050
	
	
	
	
	
	X
	
	

	Total Nickel mg/l
	2.0
	0.185
	
	
	
	
	
	X
	
	

	Soluble Nickel mg/l
	2.0
	0.073
	
	
	
	
	
	X
	
	

	Total Cobalt mg/l

(Co)
	0.5
	0.051
	
	
	
	
	
	X
	
	

	Soluble Cobalt mg/l

(Co)
	0.5
	0.050
	
	
	
	
	
	
	
	

	Free and Fixed Ammonia as Nitrogen mg/l
	5.0
	0.063
	
	
	
	
	
	
	
	

	Oxygen Demand (PV4) mg/l
	3.0
	0.484
	
	
	
	
	
	
	
	

	Arsenic mg/l (As)
	0.3
	0.010
	
	
	
	
	
	
	
	

	Cadmium mg/l (Cd)
	0.1
	0.010
	
	
	
	
	
	
	
	

	Lead mg/l (Pb)
	0.5
	0.011
	
	
	
	
	
	
	
	

	Zinc mg/l (Zn)
	1.0
	0.016
	
	
	
	
	
	
	
	

	Mercury mg/l (Hg)
	0.05
	0.010
	
	
	
	
	
	
	
	


Limits in Italics


---- denotes no limit

* Not a release, abstraction temperature at NGR SN 6955 0145

Date:   As Per Email
Richard De Filippo Sustainability Supervisor
Signed on behalf of Vale Europe Limited.,

Form W1 30/06/2020
Email to: industryregulation.swwales@cyfoethnaturiolcymru.gov.uk

