# Natural Resources Wales permitting decisions

# Bespoke permit

We have decided to grant the permit for Abergavenny 3 -19 King Henry III School operated by Morgan Sindall Construction and Infrastructure Ltd

The application number is PAN-019858

The permit number is EPR/CB3997ZY

This permit regulates the discharge site drainage into an unnamed stream of the Afon Cibi. The site drainage originates from a building site at King Henry VIII school site as it is being re-developed to include the construction of Abergavenny 3 -19 school.  The site drainage will consist of collected surface water run-off that will be captured through land drains on site. These land drains are terminated within the Swale. Silt water from the swale is then pumped back out to the TT10 treatment tank, where it is dosed with 60mg/l Ferric Chloride, a coagulant and 40mg/l Anionic flocculant. From there it passes to a lamella plate settlement tank before it is discharged to the stream. The maximum flow rate is 15 litres/second, with a maximum daily rate of 432m3/day. The applicant is currently discharging into the foul sewer at Llanfoist through a DCWW trade effluent consent. This is due to expire in September and the applicant would like an NRW permit for this discharge as the current consent they have only allows for a maximum of 5 litres/second which will need to be exceeded during higher rainfall events, which are more likely to occur in autumn/winter months.

We consider in reaching that decision we have taken into account all relevant considerations and legal requirements and that the permit will ensure that the appropriate level of environmental protection is provided.

Purpose of this document

This decision document:

- explains how the application has been determined

- provides a record of the decision-making process

- shows how all relevant factors have been taken into account

- justifies the specific conditions in the permit other than those in our generic permit template.

Unless the decision document specifies otherwise we have accepted the applicant’s proposals.

Structure of this document

- Annex 1 the decision checklist

- Annex 2 the consultation responses

# Annex 1: decision checklist

This checklist should be read in conjunction with the Duly Making checklist.

| ### Aspect | ### Justification / Detail | Criteria met |
| --- | --- | --- |
|  |  | Yes |
| Consultation |  |  |  |
| Scope of consultation | The consultation requirements were identified and implemented. The decision was taken in accordance with RGN 6 High Profile Sites, our Public Participation Statement and our Working Together Agreements. | ü |
| ### Responses to consultation | The web publicising and consultation responses (Annex 2) were taken into account in the decision. No responses were received from web publicising. The decision was taken in accordance with our guidance. | ü |
| Operator |  |  |  |
| Control of the facility | We are satisfied that the applicant (now the operator) is the person who will have control over the operation of the facility after the grant of the permit. The decision was taken in accordance with EPR RGN 1 Understanding the meaning of operator. | ü |
| European Directives |  |  |  |
| Applicable directives | All applicable European directives have been considered in the determination of the application. | ü |
| WFD | WFD stage 2 scoping has been completed and the activity/project is considered as having no risk of causing deterioration or preventing any water body or WFD Protected Area from reaching its objectives and taking account of the advice from technical officers - is considered compliant with the WFD Regulations 2017. |  |
| The site |  |  |  |
| Extent of the site of the facility | The operator has provided a plan which we consider is satisfactory, showing the extent of the site of the facility including discharge points. A plan is included in the permit and the operator is required to carry on the permitted activities within the site boundary. | ü |
| Biodiversity, Heritage, Landscape and Nature Conservation and a designated site under the Wildlife and Countryside Act. | The application is within the relevant distance criteria of a site of heritage, landscape or nature conservation, and/or protected species or habitat . A full assessment of the application and its potential to affect the site has been carried out as part of the permitting process. We consider that the application will not affect the features of the site. | ü |
| Habitat Regulation Assessment for a designated site under the EU Habitats Directive | Appropriate assessment: In light of the conclusions of an appropriate assessment, and taking account of the advice received from protected sites advisors, it has been established that the project will not adversely affect the integrity of any Natura 2000/Ramsar site, taking into account any conditions or restrictions as applicable, either alone or in-combination with other plans and projects. (As documented in section 4 of OGN 200 form 1, and section 5 if applicable). |  |
| Environmental Risk Assessment and operating techniques |  |  |  |
| Environmental risk | We have carried out a risk assessment on behalf of the operator. The operator considers this risk assessment is satisfactory. The assessment shows that, applying the conservative criteria in our guidance on Environmental Risk Assessment, all emissions may be categorised as environmentally insignificant. | ü |
| Operating techniques | We have reviewed the techniques used by the operator and compared these with the relevant guidance notes. The proposed techniques / emission levels for priorities for control are in line with the benchmark levels contained in the TGN and we consider them to represent appropriate techniques for the facility. | ü |
| The permit conditions |  |  |  |
| Emission limits | We have decided that emission limits should be set for the parameters listed in the permit. It is considered that the numeric limits described below will prevent significant deterioration of receiving waters. We have imposed numeric limits because either a relevant environmental quality or operational standard requires this. - Suspended Solids (measured after during ay 105oC) – 30mg/l - Total Iron as Fe – 1,000µg/l - pH between 6 -9 The suspended solids limits has been set in order to protect the receiving environment following consultation with the Local Environment Team. It has been set lower than the current Water Quality Standard of 50mg/l in order to protect the receiving watercourse. The total Iron limit has been set as the MAC EQS. The pH limit has been set in order to safeguard the receiving environment. | ü |
| Monitoring | We have decided that monitoring should be carried out for the parameters listed in the permit, using the methods and to the frequencies specified. These monitoring requirements have been imposed in order to comply with TGN 7.01 Section 2.4.3.2 Requirements. The operator will be required to carry out flow monitoring in accordance with these requirements. Although the discharge primarily depends on rainfall intensity we must ensure that the discharge does not cause flooding so the flow rate must not exceed 15litres/second. In addition, we must ensure that the daily volume of 432m3/day is not exceeded. We made these decisions in accordance with the Environmental Permitting Regulations 2016 and TGN EPR 7.01 “How to comply with your permit.” Based on the information in the application we are satisfied that the operator’s techniques, personnel and equipment have either MCERTS certification or MCERTS accreditation as appropriate. The operator’s equipment does not have MCERTs certification but the Local Environment Team are satisfied with the applicant’s flow meter as it can be calibrated | ü |
| Reporting | We have specified reporting in the permit. Reporting frequencies are in line with requirements set out in EPR 7.01. We made these decisions in accordance with the Environmental Permitting Regulations 2016 and TGN 7.01. | ü |
| Considerations of foul sewer | We agree with the operators justification for not connecting to foul sewer. | ü |
| Operator Competence |  |  |  |
| Environment Management System | There is no known reason to consider that the operator will not have the management systems to enable it to comply with the permit conditions. The decision was taken in accordance with RGN 5 on Operator Competence. | ü |
| Sustainable Management of Natural Resources (SMNR) |  |  |
| Considerations of SMNR - Compliance with our General Purpose | We are satisfied that this decision is compatible with our general purpose of pursuing the sustainable management of natural resources in relation to Wales and applying the principles of sustainable management of natural resources” | ü |
| Environment Wales Act 2016 |  |  |
| Biodiversity and resilience of ecosystems duty | Section 6 of the Environment Wales Act 2016 requires that we seek to maintain and enhance biodiversity in the exercise of our functions, and in so doing promote the resilience of ecosystems, in a manner that is consistent with the proper exercise of our functions. NRW is satisfied that in this case, we have taken into account and had due regard to this duty in so far as it is consistent with the function of determining an application for a stand alone water discharge activity permit under EPR2016. | ü |

# Annex 2: Consultation responses

Summary of responses to consultation, and the way in which we have taken these into account in the determination process.

Response received from

Dŵr Cymru Cyfyngedig

Brief summary of issues raised

The outflow of the proposed discharge falls within the Dwr Cymru Welsh Water (DCWW) drinking water catchment Usk at Prioress Mill which is designated as a Drinking Water Protected Area under Article 7 of the Water Framework Directive.

Summary of actions taken or show how this has been covered

Dŵr Cymru Welsh Water presumes that the applicant has consulted relevant authorities, including ourselves at Natural Resources Wales, to ensure compliance with current regulations and best practice guidelines with respect to installation and maintenance of this water treatment system. As part of the requirements from DCWW we have consulted with the relevant authorities and have ensured that the Operator has a management plan in relation to installation and maintenance of this treatment system.