## READ ME
Special Area of Conservation Permit Review - Water Discharge Activities (DCWW) - Regulation 61 Notice Response Tool
This Excel file has been put together to enable DCWW to provide a structured response to the Regulation 61 Notice for the Special Area of Conservation Permit Review.
All of the information in the 'Reg61 Response Sheet' must be completed for each asset to enable NRW to complete the Regulator Initiated Variations, use the information below to complete the sheet:
Explanation & Key Information (Reg61 Response Sheet):
  Colour Key (Row 2):
- Headings in Blue contain identification information (e.g. Permit number) or miscellaneous information that shows where further information is required (e.g. other relevant NEP Drivers to be included in variation)
- Headings in Green contain information on the permit (e.g. Permitted DWF, weir setting)
- Headings in Yellow contain information required to be provided to complete the review or allow the permit to be drafted (e.g. new P limit, site plan)
  Discharge Type:
- Columns A-V are relevant to the Final Effluent permit
- Columns W-AE are relevant to the Storm permit
- Columns AF-AJ are relevant to the Emergency permit
- Storm and Emergency information should only be complete if the permits are to be consolidated into the Final Effluent permit, if there is not a Storm/Emergency discharge at the site or if DCWW do not want a permit consolidation the boxes should contain 'N/A'
  Other:
- If there is a consolidation, new Site Plans (Column Q) and Bespoke Conditions (Column R) should consider this and include the relevant information
- If another document is required (NEP Driver Permit information/New Site Plan), it should be named in the sheet as per the document. The submission format, timing and procedure for supplyingthis information should be agreed with NRW Permitting Service

## Reg61 Response Sheet
Final Effluent Permit | [20 empty] | Storm Permit | [9 empty] | Settled Storm | [9 empty] | UV Treatment |  |  |  |  | Emergency Permit
Site Name | Permit Number | Any other permits to be consolidated into the FE permit? ▪Storm = columns V - AF ▪Settled Storm = columns AG - AP ▪UV Pre and Post Treatment = columns AQ - AU ▪Emergency = columns AV - AZ | Other NEP Driver to be included in variation? | Permitted DWF (m³/d) | FE Permit in EPR Format? | Site address | Receiving Watercourse | FE dicharge point NGR | FE sample point | UWWTD inlet sample point | UWWTD outlet sample point | MCERTS flow meter | Current Permit Limits | Bespoke Conditions Required? ▪Limits of Specified Activity ▪Operating Techniques ▪Pre-Op/Improvement Conditions | New Site Plan Required? | Site Plan File Name (.jpg or .pdf) - to include any consolidated permits | Bespoke Condition File Name (.doc) - to include any consolidated permits | Proposed Total Phosphorus as P Limit | Proposed Total Aluminium as Al Limit | Information for Other NEP Variations? (.doc, .xlsx) | Permit Number2 | Storm Permit in EPR Format? | Storm sewage discharge point | Storm sewage effluent sample point | Storm sewage discharge EDM (AMP6) NGR | Overflow setting (l/s) or weir height (if reverse flow/both) (Table S3.3) | Storm storage volume (m³) (Table S3.3) | Online or Offline storage? (Table S3.3) | Maximum size of solid matter (Table S3.3) | Screen aperture size (mm) (Table S3.3) | Permit Number3 | Settled Storm Permit in EPR Format? | Settled Storm sewage discharge point | Settled Storm sewage effluent sample point | Settled Storm sewage discharge EDM (AMP6) NGR | Overflow setting (l/s) or weir height (if reverse flow/both) (Table S3.3)4 | Settled Storm storage volume (m³) (Table S3.3) | Online or Offline storage? (Table S3.3)5 | Maximum size of solid matter (Table S3.3)6 | Screen aperture size (mm) (Table S3.3)7 | Permit Number8 | UV Treatment Permit in EPR format | UV effluent discharge point | UV pre-treatment effluent sample point | UV post-treatment effluent sample point | Permit Number9 | Emergency Permit in EPR Format? | Sewage in emergency discharge point NGR | Sewage in emergency effluent sample point NGR | PKPSM File Name (.doc)
Llandderfel Wastewater Treatment Works | CM0045201 | No | No | 22.7m³/d | Yes | Llandderfel Wastewater Treatment Works, Llandderfel Pavilion, Trafalgar Street, Llandderfel, Gwynedd, LL23 7HT | Llandderfel Mill Stream | SH 98306 36993 | SH 98310 36996 | N/A | N/A | SH 98321 37002 | LuT (95%ile) Limits: 75mg/l BOD, 150mg/l SS & 50mg/l NH3 (1st Oct-31st Mar) 25mg/l NH3 (1st Apr-30th Sept). | N/A | No | N/A | N/A | 5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 30/09/2023). | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Goytre STW Nant | AC0116401 | Yes - Settled Storm (AN0379201) | Yes - UMON3/4 | 384m³/d | No | Goytre Sewage Treatment Works, Church Road, Nantyderry, Monmouthshire, NP7 9DW | River Usk | SO 34455 05405 | SO 33054 05976 | N/A | N/A | SO 33056 05793 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS & 20mg/l NH3. Max Limits: 80mg/l BOD & 48mg/l NH3. pH 6-9 maximum range. | N/A | Yes | Permits_drawing_1_AC0116401 & Permits_drawing_2_AC0116401 | N/A | 1.4mg/l - start date 2030. | N/A | U_MON3 4 Permitting Information | N/A - (see settled storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AN0379201 | Yes | SO 34455 05405 | SO 33041 05771 | SO 33024 05772 | 11.3l/s | 126m³ | Offline | No greater than 6 mm in more than 2 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Llanbedr Wastewater Treatment Works | AA0003101 | No | No | 39m³/d | Yes | Llanbedr Wastewater Treatment Works, Maes Ffynnon, Llanbedr, Crickhowell, Powys, NP8 1SQ | Unnamed tributary of the Grwyne Fawr | SO 23819 20066 | SO 23819 20066 | N/A | N/A | N/A | LuT (95%ile) Limits: 26.5mg/l BOD, 39.5mg/l SS & 7.5mg/l NH3. | N/A |  | No | N/A | 1mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/05/2024). | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Usk STW Graig Olway Farm Llangview | AB0044801 | Yes - Settled Storm (AB0044802) | Yes - UMON3/4 | 579m³/d | No | Usk Wastewater Treatment Works, Graig Olway Farm Llangview, Usk Road, Usk, Monmouthshire, NP15 1NB | River Usk | ST 38680 99449 | ST 38971 99522 | ST 38932 99552 | ST 38971 99522 | ST 38974 99521 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS & 25mg/l NH3. Max Limits: 80mg/l BOD & 54mg/l NH3. | N/A | Yes | Permits_drawing_1_AB0044801 & Permits_drawing_2_AB0044801 | N/A | 5mg/l - start date 2030. | N/A | U_MON3 4 Permitting Information | N/A - (see settled storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AB0044802 | Yes | ST 38680 99449 | ST 38992 99556 | ST 38980 99561 | 21l/s | 214m³ | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Llangybi STW | AB0046601 | Yes - Settled Storm (AN0391001) | Yes - UMON3/4 | 204m³/d | No | Llangybi Wastewater Treatment Works, Behind Vine Tree Cottage, Llangybi, Gwent, NP15 1NP | River Usk | ST 38477 96090 | ST 37679 96603 | N/A | N/A | ST 37682 96589 | LuT (95%ile) Limits: 40mg/l BOD & 60mg/l SS. Max limit: 80mg/l BOD. | N/A | Yes | Permits_drawing_1_AB0046601 & Permits_drawing_2_AB0046601 | N/A | 5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 30/09/2023). | N/A | U_MON3 4 Permitting Information | N/A - (see settled storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AN0391001 | Yes | ST 38477 96090 | ST 37684 96585 | ST 37663 96583 | 5.3l/s | 77.4m³ | Offline | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A