Schedule 6 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	EPR/ZP3939GL

	Name of operator
	Western bioenergy

	Location of Facility
	Western Wood Energy Plant, Longlands Lane,  Margam

	Time and date of the detection 
	00:12 on 15/10/2023


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	16/10/2023 @ 09:30

	Reference or description of the location of the event 
	Hourly Average of Particulate exceeded.

	Description of where any release into the environment took place
	Main Stack

	Substances(s) potentially released
	Particulates

	Best estimate of the quantity or rate of  release of substances
	34.22 mg/m³ hourly average ( 00:00 to 00:59) 

	Measures taken, or intended to be taken, to stop any emission
	Utilisation of 4 compartment Bag Filter

	Description of the failure or accident.
	Loss of Instrument Air Pressure to Bag Filter Bypass valve causing the Bypass Damper to open momentarily.


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	Main stack

	Parameter(s)
	Particulates

	Limit
	20mg/m³

	Measured value and uncertainty
	34.22 mg/m³ hourly average ( 00:00 to 00:59)

	Date and time of monitoring
	Continuous

	Measures taken, or intended to be taken, to stop the emission
	Filter Bypass damper is installed with a Pneumatic Accumulator.


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	Particulates
	1 Hour

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	A fault was diagnosed with the main plant compressed air dryer unit where it was constantly stuck in regen mode causing an excessive demand to the instrument air system which resulted in a pressure drop. The standby dryer was isolated and not reenergised pending a maintenance outage. 

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	Staff retrained on the pre start checklists post maintenance outages to ensure backup / redundant systems are restored to correct operating conditions prior to restarting of the plant.
Also Plant driers re-configured to operate on fixed regen cycles as opposed to measured value thus eliminating random or prolonged regen operation and therefore air loss .  

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	


	Name
	Simon Thomas

	Post
	Plant Manager

	Signature
	

	Date
	16/10/2023


