INTERNAL USE ONLY

Checklist to be used when assessing Fire prevention and mitigation plans.

Please note:

this checklist has been produced to help you identify and record if the Fire Prevention and Mitigation Plan (FPMP) includes all the relevant information, in accordance with the guidance. This checklist is not a tick box exercise to enable you to determine if the plan is the suitable and each plan must be assessed and considered in terms of the risk of fire and how it will be prevented.

If you are unsure whether the proposed measures are suitable, please check with your Senior Environment/ Permitting Officer.  In addition to this some useful information has been collated on the 01. FPMP query database saved here.

(Produced in accordance with guidance Version 2, August 2017)

Application number: PAN-020465 Applicant: Denbighshire County Council Facility Address: Colomendy Waste Transfer Station, Denbighshire County Council, Waste Recycling Centre, Graig Road, Denbigh, LL16 5US Date of assessment: September/October 2023 Assessment carried out by: Louise Bailey Date FPMP submitted: V5 04/09/2023 FPMP document reference: DCC.005 Fire Prevention and Mitigation Plan (FPMP) v5.0 and V6.0 Time recording (in minutes): 530

If the applicant doesn’t follow the minimum standards in the guidance, they must be able to justify why.  The measures they take instead must be equivalent or better.  They must include detailed assessments to satisfy us that the:

- likelihood of fire

- impact from emissions during or after a fire on local people, critical infrastructure and the environment

- resources required by the Natural Resources Wales and other emergency responders during an incident

- post incident clean-up and remediation costs

are equivalent or less than would be incurred if the site followed the minimum standards in this regulatory guidance.

After you have completed your assessment, if you need to ask the operator/ applicant to submit a revised plan, you can use the same checklist to assess the revised plan. For audit purposes, it makes it easier to read the assessment If you include the “date of the plan” and use a different colored font for different plan versions.

# FPMP Checklist summary

| Section | Compliant with guidance? Yes / No / N/A | Date of plan / revised plan | Comments |
| --- | --- | --- | --- |
| 5. FPMP Contents | Y | FPMP v5.0 |  |
| 5. Site Plan | N Y | FPMP V6 |  |
| 6. Common Causes of Fires and Preventative Measures | N Y | FPMP V6 |  |
| 7. Storage Times and self-combustion factors | Y | FPMP v5.0 |  |
| 8. Managing Waste Material Stacks and Separation Distances | Y | FPMP v5.0 |  |
| 10. Baled Waste Storage | Y | FPMP v5.0 |  |
| 11. Enclosing Stacks Using Bays and Walls | Y | FPMP v5.0 |  |
| 12. Waste Stored Within a Building | Y | FPMP v5.0 |  |
| 13. Waste Stored in Containers | Y | FPMP v5.0 |  |
| 14. Layout of Waste Stacks on your Site | Y | FPMP v5.0 |  |
| 15. Seasonality and Waste Stack Management | Y | FPMP v5.0 |  |
| 16. Monitoring and Turning of Stacks | Y | FPMP v5.0 |  |
| 17. Fire Detection 18. Fire Suppression Systems | Y | FPMP v5.0 |  |
| 19. Firefighting Strategy | Y | FPMP v5.0 |  |
| 20. Water Supplies | Y | FPMP v5.0 |  |
| 21. Managing Water Run-off | Y | FPMP v5.0 |  |
| 22. Designated Quarantine Area | N Y | FPMP V6 |  |
| 23. During and After an Incident | Y | FPMP v5.0 |  |
| 24. Reviewing and Monitoring your Fire Prevention & Mitigation Plan | Y | FPMP v5.0 |  |

# Section 5 – Fire Prevention and Mitigation Plan Contents

| Does the fire prevention plan specify the following? (The guidance states that it must) | Yes/ No | NRW Comments |
| --- | --- | --- |
| A site plan | Y |  |
| the amount and type of waste received daily and how it is managed | Y | Table 2-3 of FPMP v5.0 |
| the total amount of waste and the types and forms (e.g., unprocessed, shredded, chipped, fines or baled) that are stored on site at any one time | Y | Table 2-3 of FPMP v5.0 |
| how each type of waste will be stored | Y | Table 2-3 of FPMP v5.0 |
| the maximum time each type of waste will be stored on site and how it will be managed | Y | Table 2-3 of FPMP v5.0 |
| the location within the site where each type of waste will be stored | Y | DCC.025 Waste Material Location |
| the maximum size of any waste pile (in m3), stipulating the maximum length, width, and depth | Y | Table 2-1 of FPMP v5.0 |
| the minimum separation (fire break) distance between waste piles or storage areas | Y | DCC.022 Emergency Equipment Locations & Emergency Vehicle Tracking Plan |
| A clear area must be established around the perimeter of site; this can vary depending on the layout of your site and permitted stack sizes in accordance with the separation distances as illustrated in Table 2 (this must be available at all times and identified on your site plan | Y | Site plans |
| the fire prevention techniques used, including management of hotspots (sign of potential self-combustion), monitoring, reporting, recording and actions | Y | Section 3.0 of FPMP v5.0 |
| techniques used to minimise the risk of fire spreading within the site or from the site | Y | Section 3.0 of FPMP v5.0 |
| the steps and procedures to be followed if a fire occurs on your site | Y | Section 5.0 of FPMP v5.0 |
| all combustion products and emissions (to air, land, and water) from the fire and the emergency response (including the impact on people, critical infrastructure, and the environment) and how they will be minimised. Operator needs to recognise the pollution impact of smoke and fire water and impact on environment and people. | Y | Section 6 of FPMP v5.0 |
| Contact details of sensitive receptors within 1km of your site. To protect sensitive receptors, does the plan include measures that will be used to raise the alarm and to inform local residents, e.g., local school, nursing home etc. These measures will be site specific. Operator may need to check emergency planning procedures with Local Authority. | Y | Section 1.4 and Appendix Table 7-1 of FPMP v5.0 |
| how safe access to the site for fire and rescue services and other emergency responders is achieved | Y | Site plans |
| Has the applicant included actions to be taken should a fire occur such as: | Yes/ No | Comments |
| reducing the amount of firewater run-off generated - use sprays and fogs rather than jets | n/a | Not proposed |
| recycling firewater if it’s not hazardous and it’s possible to reuse | n/a | Not proposed |
| applying water to cool unburned material and other hazards, taking care to prevent this water causing or adding to water pollution and/or increasing air pollution | n/a | Not proposed |
| separating unburned material from the fire using heavy plant | Y | Section 5.2 of FPMP v5.0 |
| separating burning material from the fire to quench it with hoses or in pools or tanks of water (this will reduce the amount of firewater produced) | n/a | Not proposed |
| using soil, sand, crushed brick and/or gravel (if smoke is threatening local communities) to help suppress the fire, although you can only do this when: | n/a | Not proposed |
| - groundwater vulnerability is low |  |  |
| - agreed as a part of a firefighting strategy by the FRS and supported by NRW |  |  |
| - contaminated material is removed and legally disposed of as soon as it is safe to do so |  |  |
| To decide which of these options, or combinations of options, is appropriate the applicant must consider the following. Have they considered these? | Yes/ No | Comments |
| scale and nature of the environmental hazards on site and the activities that take place on it | Y |  |
| risks posed to people, the environment and property | Y |  |
| type of materials you store on site, the form they’re stored in and the length of time needed to extinguish a fire involving them | Y |  |
| availability of firewater containment facilities | Y |  |
| local topography, weather conditions and fire scenarios that could reasonably be expected on site | Y |  |

# Section 5 - Site Plan

(Could consist of location plan, site plan and drainage plans on one or more plan)

| Does the site plan include the following: The FPMP must include a site plan(s) drawn to scale showing: | Yes/ No | NRW Comments |
| --- | --- | --- |
| layout of buildings | Y | DCC.025 Waste Material Location |
| any areas where hazardous materials are stored on site (location of gas cylinders, process areas, chemicals, piles of combustible materials, oil, and fuel tanks) | Y | DCC.025 Waste Material Location |
| main access routes for fire engines and any alternative access | Y | DCC.022 Emergency Equipment Locations & Emergency Vehicle Tracking Plan |
| access points around the site perimeter to assist firefighting – see table in guidance for typical FRS vehicle access requirements | Y | DCC.022 Emergency Equipment Locations & Emergency Vehicle Tracking Plan |
| hydrants and water supplies | Y | DCC.022 Emergency Equipment Locations & Emergency Vehicle Tracking Plan DCC.021 Site Drainage Plan |
| any watercourse, borehole or well located within or near the site | n/a |  |
| areas of natural and unmade ground | Y | DCC.024 Site Surfacing Plan |
| the location of plant, protective clothing and pollution control equipment and materials | Y | DCC.022 Emergency Equipment Locations & Emergency Vehicle Tracking Plan |
| drainage systems, foul and surface water drains, and their direction of flow and outfall points | Y | DCC.021 Site Drainage Plan |
| the location of drain covers and any pollution control features such as drain closure valves and firewater containment systems | Y | DCC.021 Site Drainage Plan |
| location of “off- site” emergency information pack with site plan (as specified above) |  | “Copies of this FPMP are kept on site, in the site office and in the weighbridge office, and are accessible to all personnel.” Not shown on site plans 26/10/2032- updated in DCC.005 Fire Prevention and Mitigation Plan (FPMP) v6.0 and DCC.022 Emergency Equipment Locations & Emergency Vehicle Tracking Plan v2.0 |
| location of key receptors such as critical infrastructure, schools, hospitals, residential areas, workplaces, protected habitats, and rivers within 1km of the site | Y | Figure 1-5 of FPMP |
| Location of the quarantine area | Y | DCC.025 Waste Material Location Plan (and on multiple other plans- all give the same location) |
| compass rose showing north and the prevailing wind direction | Y | Windrose is in Figure 2-4 of DCC.002 Environmental Risk Assessment v4.0 |

# Section 6 - Common causes of fires and preventative measures

| The FPMP should consider where applicable the common causes of fire, some won’t apply, others need to be included | Yes/ No | NRW Comments |
| --- | --- | --- |
| arson or vandalism | Y | Table 2-4 of FPMP v5.0 |
| Visitors & contractors | Y | Section 2.1 of FPMP v5.0 |
| Ignition sources | Y | Table 2-4 of FPMP v5.0 |
| self-combustion (e.g., due to chemical oxidation) | Y | Table 2-4 of FPMP v5.0 |
| plant or equipment failure | Y | Table 2-4 of FPMP v5.0 |
| discarded smoking materials | Y | Table 2-4 of FPMP v5.0states “n/a” |
| hot works (e.g., welding or cutting) | Y | Table 2-4 of FPMP v5.0 |
| industrial heaters | Y | Table 2-4 of FPMP v5.0 |
| Plant & hot exhausts | Y | Table 2-4 of FPMP v5.0 |
| damaged or exposed electrical cables | Y | Table 2-4 of FPMP v5.0states “n/a” |
| Reaction between wastes | Y | Table 2-4 of FPMP v5.0 |
| hot loads deposited at the site | Y | Table 2-4 of FPMP v5.0 |
| Build up loose combustible waste, dust, and fluff | Y | Table 2-4 of FPMP v5.0 |
| “Tramp” metal | Y | Table 2-4 of FPMP v5.0 |
| Batteries within waste deposits | Y | Table 2-4 of FPMP v5.0. “residual waste” is not being treated; therefore, it is unknown if these will contain batteries. 26/10/23: The 'Batteries within waste deposits' section has been updated within Table 2.4 of DCC.005. to explain further how the risk of batteries within waste streams will be managed both prior and during waste collection and upon deposit. DCC.004_EMS.S4.02_v3 has also been updated to better reflect this process. |
| Batteries in ELVs | n/a | Not an accepted waste type |
| Cylinders stored at site | n/a | Not an accepted waste type |
| Leaks and spillages of oils and fuels | Y | Table 2-4 of FPMP v5.0 |

# Section 7 - Storage times and self-combustion factors

| Self-combusting materials | Yes/ No | NRW Comments |
| --- | --- | --- |
| Is the applicant storing materials at risk of self-combustion (see list in guidance)? | Y |  |
| If yes, are they storing these in line with Table 1 – maximum storage times? | Y | Table 2-4 of FPMP v5.0 “No material that may self-combust is stored on site for more than 14 days, under standard operational circumstances.” Also see Section 2.3.4 and Table 2-3 of FPMP v5.0 |
| If the applicant is storing materials at risk of self-combustion for longer than 3 months, has the applicant demonstrated additional measures they will take, including monitoring? Guidance states they MUST | n/a | Table 2-4 of FPMP v5.0 “self-combust are only stored on site for longer than 14 days in exceptional circumstances, and never for more than 28 days.” Also see Section 2.3.4 and Table 2-3 of FPMP v5.0 |
| Has the applicant considered adopting the following fire prevention principles? (Guidance states applicant should consider) |  |  |
| reduce risk factors (e.g. exposed metal content, proportion of 'fines', mixing of materials and heat generated during treatment) | Y |  |
| minimise stacks sizes (small stacks with appropriate separation are safer than one larger one) | Y |  |
| control moisture levels | n/a | Not part of suggested procedures due to short storage times. |
| demonstrate good stock rotation for all stored materials and show how this is monitored and implemented daily | Y | Section 3.0 of FPMP v5.0 |
| store material in its largest form prior to processing e.g. do not undertake preparatory treatments such as size reduction of green waste unless you are intending on submitting the waste to the treatment process immediately | Y | Wastes accepted on site are not “processed” or made smaller |
| monitor and control sub-surface temperature and moisture content with a suitable thermal device (thermal probe/thermal camera) and ensure that this is capable of reaching all parts of a stack (if materials are stored in plastic wrapping you must demonstrate a sampling and testing protocol to ensure a representative number of bales (minimum 10%) are assessed during monitoring | n/a | Not part of suggested procedures due to short storage times. |
| routinely turn stacks | Y | Section 3.1 of FPMP v5.0 |
| detect and control hotspots within stacks (Note: steam is a good indicator of self-heating) | n/a | Not part of suggested procedures due to short storage times. |
| define the maximum storage time of all materials on site and show how this will be monitored and controlled | Y | Section 3.1 of FPMP v5.0 |
| minimise external heating during hot weather by shading from direct sunlight | Y | Waste stored in buildings or covered bays. |

# Section 8 - Managing Waste Material Stacks and Separation Distances

| Guidance says MUST be used | Yes/No | NRW Comments |
| --- | --- | --- |
| Are stack lengths and separation distances in line with Graph 1 for general wastes such as RDF, SRF (Refuse derived fuel/solid recovered fuel - various types of fuel derived from wastes using various treatment processes), wood, paper etc. | Y | Table 2-1 of FPMP v5.0 and DCC.022 Emergency Equipment Locations & Emergency Vehicle Tracking Plan All waste is to be stored in bays or containers. |
| Are stack lengths and separation distances in line with Graph 2 for plastics and rubber wastes? | Y | Table 2-1 of FPMP v5.0 and DCC.022 Emergency Equipment Locations & Emergency Vehicle Tracking Plan All waste is to be stored in bays or containers. |
| Graphs 1 and 2 assume a stack height of 4m, if stack sizes are significantly lower bespoke separation distances can be used – does this apply? | n/a | While stack heights are lower than 4 meters, bespoke distances have not been proposed |
| Has a competent fire engineer been used to calculate any bespoke separation distances? | n/a |  |
| Storage of whole end of life vehicles (ELVs) Applicant MUST set out in the FPMP how they will store ELVs |  |  |
| Is each vehicle accessible from at least one side allow a fire to be fought and so unburnt vehicles can be accessed and moved to prevent the fire spreading (These rules will limit any row to a depth of 2 vehicles.) | n/a | Not a proposed waste |
| If the applicant proposes to store vehicles one on top of another, or on racking, they should limit this to 3 vehicles high so the stack can remain stable during a fire. You should maintain a minimum separation distance between rows or blocks of vehicles in accordance with Table 2 (depending on the length of the rows) | n/a | Not a proposed waste |
| As part of the applicants’ waste stack management protocol, they should consider adopting the following general fire prevention and mitigation principles: | Yes/No |  |
| manage all stacks to within the maximum sizes and minimum separation distances | Y |  |
| have availability to adequate water supplies or alternative firefighting methods at all times to fight a fire | Y |  |
| enable easy access for emergency vehicles around the whole site | Y |  |
| manage all stacks of materials that can self-combust and demonstrate suitable additional precautions if they are stored for more than 3 months | n/a |  |

# Section 10 - Baled waste storage

| The guidance states the FPMP MUST show how they are reducing the risk of fire occurring in bales. | Yes/ No | NRW Comments |
| --- | --- | --- |
| Does the applicant show how they are reducing the risk of fire occurring in bales? | Y | Section 2.3.1 of FPMP v5.0 |
| In regard to baled waste storage, it is RECOMMENDED the FPMP show: |  |  |
| what sampling and testing protocol you will use to make sure you assess a representative number of bales (minimum 10%) during monitoring | n/a | Not proposed due to short storage times |
| that you get representative temperature readings from the centre of the bales; and from bales within the centre of each stack pile | n/a | Not proposed due to short storage times |
| that you turn the bales to make sure the waste stays cold | Y | Sections 3.1 and 3.2 of FPMP v5.0 |
| If baled waste may exceed limits in Table 1, have additional measures, such as breaking and rewrapping bales been taken? Have additional fire risks that may be introduced from such measures been addressed e.g., sudden introduction of oxygen | n/a | Not exceeding limits in Table 1 |
| What is the storage configuration of the bales? Has any fire risk from the configuration been addressed? | Y | Pyramid stack- Section 2.3.1 of FPMP v5.0 |

# Section 11 - Enclosing stacks using bays and walls

| Guidance states the bays and/or walls SHOULD be able to provide the following | Yes/ No | NRW Comments |
| --- | --- | --- |
| 120 minutes’ fire resistance period | Y | Sections 2.3.1, 2.3.2, 3.3 and Appendix 7.2 of FPMP v5.0 |
| The guidance states that the product specification will need to be established via approved stockiest to ensure appropriate standard of fire resistance are met. |  |  |
| Has the applicant provided this evidence? | Y | Appendix 7.2 of FPMP v5.0 |
| The guidance states: “it is essential that when installing such products that the installation method used is in line with the manufacturers recommended installation requirements. |  |  |
| Has the applicant provided evidence of this or confirmed in their FPMP that installation method used is in line with the manufacturers recommended installation requirements? | Y | Appendix 7.2 of FPMP v5.0 |
| The guidance states that the FPMP SHOULD demonstrate: |  |  |
| full and frequent stock rotation and how this will be monitored and recorded | Y | Section 3 of FPMP v5.0 |
| protection from wind | Y | Waste will be stored in buildings or bays |
| how you intend to check temperature and moisture content of all the material within the bay so that the entire volume of the pile receives representative checks | n/a | Not part of suggested procedures due to short storage times. |
| t the construction of the walls in terms of how they offer a thermal barrier and enable cooling | Y | Sections 2.3.1, 2.3.2, 3.3 and Appendix 7.2 of FPMP v5.0 |
| how stock capacity will be managed and controlled | Y | Section 3.1 of FPMP v5.0 |
| how you will ensure segregation of materials | Y | See waste acceptance procedures |
| how calculation of flame height and radiation has been taken into account in preventing the spread of fire between piles | Y |  |
| prevention of brands or lighted material moving outside the bay walls | Y |  |
| prevention of bridging across or around walls | Y |  |
| how a ‘freeboard’ space at the top and sides of the walls will be physically retained at all times in accordance with the latest available guidance | Y |  |
| the frequency and method of turning piles | Y | Section 3.1 of FPMP v5.0 |
| how the quarantine area will be used and how materials will be moved during an incident. |  | Some information in Section 2.2 of the FPMP v5.0 |

# Section 12 - Waste stored within a building

| If the applicant is storing waste in a building, the guidance states they SHOULD adopt the following principles at all times | Yes/ No | NRW Comments |
| --- | --- | --- |
| Ensure waste stack sizes and separation distances are appropriate to the risk. Table 2 can be used as a starting point but not absolute guidance for internal storage. General principles should be adopted: | Y |  |
| Consider the use of fire walls/bunkers. | Y | Section 2.3.2 and Appendix 7.2 of FPMP v5.0 |
| Separation between internally stored wastes and building walls, plant & other equipment within buildings will need to be considered. In general fires in internally stored wastes are far more likely to spread to buildings and plant than for externally stored wastes. As a result, your insurer is likely to place more emphasis on internal storage than external storage fire management. You should seek advice from your insurer to ensure that you have met any requirements for fire detection and fire suppression. | Y | Insurance: Section 5.1 of FPMP v5.0 |
| If you are storing wastes internally in large quantities, such as in warehousing, then you should seek competent advice on the precautions to be taken. These will depend on the type of building used, the types of waste being stored and what fire precautions are already in place. This is a specialised area, and the general standards applied to the warehousing of goods may not be appropriate to the internal storage of wastes. | n/a |  |
| If the building is heated this could affect the potential for self-heating of the waste and should be taken into account when assessing self-heating risks. | n/a | Buildings are not heated; only office will have air source heat pump |
| You must ensure that all escape routes, fire exits, alarm call points and fire extinguishers are kept clear and free from waste at all times | Y |  |
| Ensure electrical equipment and heaters are kept free from waste, including dust and packaging materials. | Y | Table 2-4 of FPMP v5.0 |
| Waste storage areas should be fire compartmented away from office areas. | Y | See site plans |
| Waste storage areas should have some means of clearing smoke from the building, such as openable skylights or roller shutter doors, to aid firefighting. | Y |  |

# Section 13 - Waste Stored in containers

| Has the applicant included the following (guidance states you must): | Yes/ No | NRW Comments |
| --- | --- | --- |
| If you store waste in containers that can hold more than 1,100 litres, each one must be accessible so any fire inside it can be extinguished, for all other containers holding waste, the appropriate stack sizes apply as per Table 2 | n/a | Max container size is 1,100 litres- section 2.3.3 of FPMP v5.0 |
| Guidance states the applicant SHOULD manage containers as follows: |  |  |
| Shipping containers should be stacked no more than 2 containers high and secured with a lock outside of operational hours. | n/a | Waste not being stored in shipping containers |
| If you have a fire, you should be able to move containers as soon as is reasonably practicable in a safe manner to prevent the fire spreading. You should set out in your FPMP the procedures you will put in place to allow this to happen. | Y | Section 2.3.3 of FPMP v5.0 |

# Section 14 - Layout of waste stacks on your site

| In addition to stack sizes, storage methods/types and appropriate separation distances, has the applicant taken into consideration the following factors? (Guidance says these factors MAY need to be taken into account) | Yes/No | NRW Comments |
| --- | --- | --- |
| Location of potential ignition sources on your site | Y |  |
| Location/s of occupied buildings and high-asset value equipment and plant | Y |  |
| Escape and evacuation routes around your site and within buildings must not be compromised by stack layout | Y |  |
| Location of flammable and/or hazardous substances kept on site, such as gas cylinder cages, diesel tanks, quarantine areas which may contain non-conforming wastes etc. | Y |  |
| Locations of on or off-site fire hydrants, other water supplies and fire-fighting equipment – you do not want to block access to these with your stack layout | Y |  |
| Proximity and location/s of any infrastructure which may be affected by a fire, such as overhead power lines, major roads, rail lines etc. | Y |  |
| Proximity and location/s of any off-site, third party buildings which may be affected by a fire | Y |  |
| Permitted amounts of wastes, and types of waste, allowed on site | Y |  |
| Location of a ‘quarantine’ area, as appropriate to site specifics | Y |  |
| Operational practicalities such as movements of vehicles & designated routes | Y |  |
| Stock rotation requirements, seasonality of supply/off-take etc. | Y |  |
| The applicant should also consider |  |  |
| the prevailing wind, where fire water will flow and the firefighting strategy that will be used. | Y |  |

# Section 15 - Seasonality and waste stack management

| Has the applicant included the following (guidance states they SHOULD): | Yes/ No | NRW Comments |
| --- | --- | --- |
| provide a technical assessment that shows you have confidence that your proposal will be viable in foreseeable market conditions – this should prove the suitability of materials, the resilience of the supply chain and end user outlets | n/a | Not relevant to type of permit applied for |
| If the materials on your site are subject to seasonal variation in demand and/or supply you should demonstrate how you intend to manage these variations. You should be able to demonstrate how you will follow the principle of “first in, first out” so that wastes are stored for no longer periods than indicated in Table 1. | Y | Sections 2.3.5 and 3.1 of FPMP v5.0 |

# Section 16 - Monitoring and turning of stacks

| Has the applicant stated how they will achieve this and included the following? (Guidance states they should) | Yes/ No | NRW Comments |
| --- | --- | --- |
| The staff must be trained to detect and manage hotspots. | Y | Section 3 of FPMP v5.0 |
| Piles are monitored regularly and temperature increases and changes in moisture content are minimised. | Y | Section 3 of FPMP v5.0 |
| The equipment they use to detect temperature and moisture content must be capable of operating at any depth throughout the pile. Therefore, if they are proposing to have a stack 4m deep, their probe must be capable of operating the depth of the proposed stack. | n/a | Section 3 of FPMP v5.0 |
| They must explain what indicators they will use in relation to temperature and moisture content and the escalation of actions in relation to these indicators. | Y | Section 3 of FPMP v5.0 |

# Section 17 Fire detection and Section 18 fire suppression systems

| Has the applicant included the following (guidance states they SHOULD): | Yes/ No | NRW Comments |
| --- | --- | --- |
| When deciding what type of system to install you need to take into account that: - the fire and rescue service may not be able to enter the building during a fire - a suppression system may not extinguish a fire, although it may prevent a fire spreading and then allow the fire to be fought effectively by the fire and rescue service - the water supply to a fire system is reliable and adequate at all times | Y | Section 4.3 of FPMP v5.0 |
| Has the applicant considered fitting the following? (Guidance states that they SHOULD consider) | Yes/ No | Comments |
| automatic detection systems such as: |  |  |
| - smoke and heat detectors including temperature probes | Y | Section 4.3 of FPMP v5.0 |
| - CCTV visual flame detection systems |  |  |
| - spark, infrared and ultraviolet detection |  |  |
| fire suppression systems such as: |  |  |
| - sprinklers | n/a | Not proposed |
| - manual open deluge system |  |  |
| - deluge/water spray systems |  |  |
| - water monitors/cannons/curtains |  |  |

# Section 19 - Firefighting Strategy

| Does the applicant have the following resources? (Guidance does not state whether they must have these or need to consider these) | Yes/No | NRW Comments |
| --- | --- | --- |
| (suitable) heavy mobile plant you have available that can be used to move waste around the site, for example loaders, excavators, material handlers | n/a | Not mentioned |
| the use of portable water carriers/bowsers can prove to be an essential mechanism to help extinguish fire effected waste | n/a | Not mentioned |
| adequately trained staff available | Y | Section 2.1 of FPMP v5.0 |
| available water supply | Y |  |
| finances available for additional resources | Y |  |
| Has the applicant described the firefighting techniques that would be employed using the said resources? (Guidance does not state whether they must have these or need to consider these) | Yes/No | Comments |
| applying water to cool unburned material and other hazards | N/A | Not proposed |
| separating unburned material from the fire using appropriate heavy plant | Y |  |
| separating burning material from the fire to quench it with hoses or in pools or tanks of water | N/A | Not proposed |
| suffocating the fire using soil, sand, crushed brick or gravel. However, you can only do this if:  Natural Resources Wales has agreed you can do this in the first instance, and  you remove and dispose of contaminated material as soon as it is safe to do so | N/A | Not proposed |

# Section 20 - Water supplies

| Have they considered the following? (Guidance states applicant MUST have adequate water supplies) | Yes/ No | NRW Comments |
| --- | --- | --- |
| Has the applicant demonstrated that they would have sufficient water supplies available on their site to manage a worst-case scenario incident | Y | Section 4.2 of FPMP v5.0 |
| Has the applicant described what form their water supply is in? This could be water in storage tanks or lagoons on site, or access to hydrants or mains water supply for example. | Y | Section 4.2 of FPMP v5.0 Water tank fed by mains supply. |
| Has the applicant referred to alternative water supplies such as a near-by river, canal, lake, lagoon etc. (in some rare cases wells can be used, but their capacity and recharge characteristics must be adequate)? These can be considered within their plan to supplement tanked or mains supplies however these alternative supplies need to be capable of being accessed promptly. | Y | Section 4.2 of FPMP v5.0 Hydrants as back up only |

# Section 21 - Managing fire water run-off

The containment facilities and pollution equipment they need will depend on the size of the site, the amount of material they store and the firefighting strategy.  The CIRIA document 'Containment systems for the prevention of pollution (C736)' may help you identify the facilities and equipment you need for your site.

| The FPMP MUST set out how they will prevent fire water affecting the following receptors? | Yes/ No | NRW Comments |
| --- | --- | --- |
| The local groundwater and surface water bodies | Y | Section 4.2 of FPMP v5.0 Fire water will be stored on site |
| Any well, spring or borehole within 50m used for the supply of water for human consumption, including private water supplies | Y | Section 4.2 of FPMP v5.0 Fire water will be stored on site |
| Have they considered the following? (Guidance states applicant SHOULD be able to contain run-off | Yes/ No | NRW Comments |
| Where is run off going to? If it is to sewer, a written agreement must be in the FPMP from the sewerage undertaker | Y | Section 4.2 of FPMP v5.0 Fire water will be stored on site, then pumped and tankered off site by a licensed hazardous waste carrier after the fire. |
| How will they contain fire water? Has any secondary or tertiary containment been specified? | Y | Section 4.2 of FPMP v5.0 Fire water will be stored on site, then pumped and tankered off site by a licensed hazardous waste carrier after the fire. |
| Are their measures suitable? This will depend on the size of the site, the amount of combustible material stored and the firefighting strategy | Y |  |
| Is there an environmental risk to the surrounding area? Groundwater/ watercourses/ habitats etc. | N |  |

# Section 22 - Designated quarantine area

| Has the applicant included the following (guidance states they SHOULD) | Yes/ No | NRW Comments |
| --- | --- | --- |
| the location of this area and the volume of waste that it can hold | Y | DCC.025 Waste Material Location Plan (and on multiple other plans- all give the same location) |
| Is the quarantine area within the permitted boundary area of the site (guidance states it should) | Y | DCC.025 Waste Material Location Plan (and on multiple other plans- all give the same location) |
| Does the quarantine area hold at least 50% of the volume of the largest stack, | Y | Section 4.1 of FPMP v5.0 |
| Does the quarantine area have a separation distance of at least 6 metres around the quarantined waste (this can be decreased if concrete bunkers/walls will be used) | Y |  |
| If material is to be stored temporarily in the quarantine area, are procedures in place to move the material as soon as is practicable. These procedures should be included in the FPMP. Are these included? | Y | Section 5.2 of DCC.005 has been updated with the procedure for removing non-fire related quarantine waste from the quarantine area in the event of a fire. |

# Section 23 - During and after an incident

| The FPMP must have contingency measures in place for dealing with issues during and after a fire (Guidance states they MUST) | Yes/ No | NRW Comments |
| --- | --- | --- |
| diverting incoming wastes to alternative sites during a fire | Y | Section 5.3 of FPMP v5.0 |
| having a plan for how you will notify those who may be affected by a fire, such as nearby residents and businesses | Y | Section 1.4 of FPMP v5.0 |
| contractors that might be used to assist with additional plant for firefighting techniques, removal of waste material, containment and removal of excess water run-off | Y | Section 5.3 and 4.2 of FPMP v5.0 |
| how you will clear and decontaminate the site | Y | Sections 5.5 and 5.6 of FPMP v5.0 |
| the steps you must take before the site can become operational again | Y | Sections 5.5 and 5.6 of FPMP v5.0 |

# Section 24 - Reviewing and Monitoring your Fire Prevention & Mitigation Plan

| The guidance states that FPMP SHOULD be treated as a live document | Yes/ No | NRW Comments |
| --- | --- | --- |
| Has the applicant described methods and procedures used to maintain compliance as a separate section within your Fire Prevention and Mitigation Plan? | Y | Throughout FPMP v5.0 |
| Have they stated the circumstances that would warrant a review, these could include: - Experiencing a fire incident. Following any fire, it is essential that your FPMP (and overall fire management measures) should be reviewed and improved as required to address any issues/concerns - Additional combustible waste streams accepted on site. - Increase waste volumes accepted. - Development of site infrastructure – new buildings. - Installation of new equipment or plant – baler/loading shovel/sort-line/trommel etc. | Y | Sections 1.1, 2.1, 5.0, 5.1, and 5.6 of FPMP v5.0 |
| Have they described the areas of the FPMP that would need updating because of said circumstances? (See the guidance for examples) | Y | Sections 1.1, 2.1, 5.0, 5.1, and 5.6 of FPMP v5.0 |