Permit Number: 
BR8212IK





Operator: 

Knauf Insulation Ltd
Installation:

Knauf Insulation Ltd, Cwmbran


Form Number:
Water2 
Reporting of emissions to water (other than to sewer) for the period from 
01/01/2019
to
30/06/2019
	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Reference Period
	Result [1]
	Test

Method [2]
	Sample

Date and Times [3]
	Uncertainty

[4]

	W1
	COD
	<10 mg/l
	Spot sample
	<10 mg/l
	AES 1029
	25/06/2019
09:30
	-

	W1
	Total suspended solids
	<5.0 mg/l
	Spot sample
	<5.0 mg/l
	AES 1041
	25/06/2019
09:30
	-

	W1
	Total hydrocarbon oil
	15 mg/l
	Spot sample
	<0.01 mg/l
	AN 34
	25/06/2019
09:30
	-

	W1
	PH max
	9
	Spot sample


	7.3
	AES 1035
	25/06/2019
09:30
	-

	
	
	
	
	
	
	
	

	W1
	PH min
	6
	Spot sample
	7.3
	AES 1035
	25/06/2019
09:30
	-


[1]
The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

[2]
Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. gas chromatography.
[3]
For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   

[4]
The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.
Signed …… …………………[image: image1.emf]…………………………………….  

Date…19/07/2019…..


(Authorised to sign as representative of Operator)

