## READ ME
Special Area of Conservation Permit Review - Water Discharge Activities (DCWW) - Regulation 61 Notice Response Tool
This Excel file has been put together to enable DCWW to provide a structured response to the Regulation 61 Notice for the Special Area of Conservation Permit Review.
All of the information in the 'Reg61 Response Sheet' must be completed for each asset to enable NRW to complete the Regulator Initiated Variations, use the information below to complete the sheet:
Explanation & Key Information (Reg61 Response Sheet):
  Colour Key (Row 2):
- Headings in Blue contain identification information (e.g. Permit number) or miscellaneous information that shows where further information is required (e.g. other relevant NEP Drivers to be included in variation)
- Headings in Green contain information on the permit (e.g. Permitted DWF, weir setting)
- Headings in Yellow contain information required to be provided to complete the review or allow the permit to be drafted (e.g. new P limit, site plan)
  Discharge Type:
- Columns A-V are relevant to the Final Effluent permit
- Columns W-AE are relevant to the Storm permit
- Columns AF-AJ are relevant to the Emergency permit
- Storm and Emergency information should only be complete if the permits are to be consolidated into the Final Effluent permit, if there is not a Storm/Emergency discharge at the site or if DCWW do not want a permit consolidation the boxes should contain 'N/A'
  Other:
- If there is a consolidation, new Site Plans (Column Q) and Bespoke Conditions (Column R) should consider this and include the relevant information
- If another document is required (NEP Driver Permit information/New Site Plan), it should be named in the sheet as per the document. The submission format, timing and procedure for supplyingthis information should be agreed with NRW Permitting Service

## Reg61 Response Sheet
Final Effluent Permit | [23 empty] | Storm Permit | [9 empty] | Settled Storm | [9 empty] | UV Treatment |  |  |  |  | Emergency Permit
Site Name | Permit Number | Permitting officer allocated to | PAN | Any other permits to be consolidated into the FE permit? ▪Storm = columns V - AF ▪Settled Storm = columns AG - AP ▪UV Pre and Post Treatment = columns AQ - AU ▪Emergency = columns AV - AZ | Other NEP Driver to be included in variation? | Permitted DWF (m³/d) | FE Permit in EPR Format? | Site address | Receiving Watercourse | FE dicharge point NGR | FE sample point | UWWTD inlet sample point | UWWTD outlet sample point | MCERTS flow meter | Current Permit Limits | Bespoke Conditions Required? ▪Limits of Specified Activity ▪Operating Techniques ▪Pre-Op/Improvement Conditions | New Site Plan Required? | Site Plan File Name (.jpg or .pdf) - to include any consolidated permits | Bespoke Condition File Name (.doc) - to include any consolidated permits | Proposed Total Phosphorus as P Limit | Proposed Total Iron as FE Limit | Proposed Total Aluminium as Al Limit | Information for Other NEP Variations? (.doc, .xlsx) | Permit Number | Storm Permit in EPR Format? | Storm sewage discharge point | Storm sewage effluent sample point | Storm sewage discharge EDM (AMP6) NGR | Overflow setting (l/s) or weir height (if reverse flow/both) (Table S3.3) | Storm storage volume (m³) (Table S3.3) | Online or Offline storage? (Table S3.3) | Maximum size of solid matter (Table S3.3) | Screen aperture size (mm) (Table S3.3) | Permit Number | Settled Storm Permit in EPR Format? | Settled Storm sewage discharge point | Settled Storm sewage effluent sample point | Settled Storm sewage discharge EDM (AMP6) NGR | Overflow setting (l/s) or weir height (if reverse flow/both) (Table S3.3) | Settled Storm storage volume (m³) (Table S3.3) | Online or Offline storage? (Table S3.3) | Maximum size of solid matter (Table S3.3) | Screen aperture size (mm) (Table S3.3) | Permit Number | UV Treatment Permit in EPR format | UV effluent discharge point | UV pre-treatment effluent sample point | UV post-treatment effluent sample point | Permit Number | Emergency Permit in EPR Format? | Sewage in emergency discharge point NGR | Sewage in emergency effluent sample point NGR | PKPSM File Name (.doc)
LLANIGON Wastewater Treatment Works | AW1003701 | Kristina Jenkins | PAN-021919 | No | No | 32.3 | Yes | Llanigon WwTW, Lower Sheep House Cottages, Hay-on-Wye, Hereford, HR3 5PR | Digedi Brook | SO 20468 40493 | SO 20466 40524 | N/A | N/A | SO 20466 40524 | LuT (95%ile) Limits: 31mg/l BOD, 34mg/l SS. | N/A | Yes | AW1003701 Site Plan | N/A | 0.8mg/l - 31/03/2035 start date | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
BRECON STW BRECON WWTW BRECON POWYS | AB0041501 | Marc Campbell | PAN-021959 | Yes - Settled Storm (AB0041502) | No | 2887 | No | Brecon WwTW, Brecon, Powys, LD3 7PL | River Usk | SO 05921 27595 | SO 05756 27583 | SO 05592 27697 | SO 05756 27583 | SO 05752 27587 | LuT (95%ile) Limits: 37mg/l BOD, 55mg/l SS, 15mg/l NH3. Maximum Limits: 74mg/l BOD, 44mg/l NH3, pH value 6-9 (maximum range). | N/A | Yes | AB0041501 Site Plan | N/A | 2mg/l - 31/03/2025 start date | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AB0041502 | Yes | SO 05921 27595 | SO 05732 27574 | SO 05732 27574 | 78.6 l/s | 566 | Off-line | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANELLEN STW LLANELLEN MONMOUTHSHE | AB0046101 | William Comfort | PAN-021981 | No | No | 107.5 | No | Llanellen STW, Llanellen | River Usk | SO 30349 11128 | SO 30349 11128 | N/A | N/A | SO 30310 11090 | LuT (95%ile) Limits: 65mg/l BOD, 100mg/l SS. | N/A | Yes | AB0046101 Site Plan | N/A | 5mg/l - insufficient samples to accept backstop immediately (samples collected by October 23) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANYBYDDER WWTW CEREDIGION | BJ0091401 | Emma Dulson | PAN-021522 | Yes - Settled Storm (BJ0091402) & Emergency (BJ0091405) | Yes - U_MON3&4 for SS permit BJ0091402 | 1019 | No | Llanybydder WwTW, Llanybydder, Near Lampeter, Ceredigion, SA40 9SD | River Teifi | SN 51724 43265 | SN 51602 43144 | N/A | N/A | SN 51939 43401 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 5mg/l NH3. Maximum Limits: 80mg/l BOD, 20mgl NH3, pH value 6-9 (maximum range). | N/A | Yes | Permits_drawings_1_BJ0091402 | N/A | 2.5mg/l - 31/03/2025 start date | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | BJ0091402 | Yes | SN 51850 43362 | SN 51935 43399 | SN 51930 43406 | 27.5 l/s | 63 | Off-line | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | BJ0091405 | No | SN 52815 44473 | SN 52834 44445 | BJ0091401 PSKPM
BUILTH WELLS STW | AW1000701 | Tom Dauncey | PAN-021269 | Yes - Settled Storm & Emergency (NPSWQD009903) | Yes - U_MON3&4 | 1622 | No | Builth Wells WwTW, Builth Wells, Powys, LD2 3BP | River Wye | SO 04552 51471 | SO 04575 51446 | SO 04566 51443 | SO 04575 51446 | SO 04623 51479 | LuT (95%ile) Limits: 25mg/l BOD, 45mg/l SS, 30mg/l NH3. Maximum Limits: 60mg/l BOD, 61mg/l NH3 | N/A | Yes | Permits_drawings1_NPSWQD009903 | N/A | 5mg/l - insufficient samples to accept backstop immediately (samples collected by October 23) | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NPSWQD009903 | Yes | SO 04552 51471 | SO 04569 51450 | SO 04567 51449 | 40 l/s | 150 | Off-line | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | NPSWQD009903 | No | SO 04552 51471 | SO 04565 51447 | AW1000701 PSKPM
TALGARTH STW BRONLLYS ROAD TALGARTH | AW1005301 | Tom Dauncey | PAN-021403 | Yes - Settled Storm (AN0373401) | Yes - U_MON3&4 for SS Permit AN0373401 | 841 | Yes | Talgarth WwTW, Bronllys Rd, Talgarth, LD3 0HL | Afon Llynfi | SO 15073 34806 | SO 15206 34778 | SO 15240 34778 | SO 15206 34778 | SO 15257 34788 | LuT (95%ile) Limits: 28mg/l BOD, 45,g/l SS, 8mg/l NH3. Maximum Limits: 63mg/l BOD, 30mg/l NH3. | N/A | No | Permits_drawings_1_AW1005301 | N/A | 0.25mg/l - 31/03/2030 start date | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AN0373401 | Yes | SO 15073 34806 | SO 15202 34782 | SO 15263 34779 | 24.9 l/s | 180 | Off-line | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANFOIST WASTEWATER TREATMENT WORKS ME | AB0038201 | Emma Dulson | PAN-021332 | Yes - Settled Storm (AB0038202) | Yes - U_MON3&4 for SS Permit AB0038202 | 5723 | No | Llanfoist WwTW, Merthyr Rd, Llanfoist, Abergavenny, NP7 2LH | River Usk | SO 30082 13206 | SO 30036 13287 | SO 30007 13234 | SO 29919 13279 | SO 29994 13247 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 21mg/l NH3. Maximum Limits: 80mg/l BOD, 49mg/l NH3, pH value 6-9 (maximum range). | N/A | Yes | Permits_drawings_1_AB0038201 | N/A | 2mg/l - 31/03/2025 start date | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AB0038202 | Yes | SO 30082 13206 | SO 29924 13300 | SO 29929 13274 | 137 l/s | 975 | Off-line | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CRICKHOWELL STW ABERGAVENNY ROAD | AC0094701 | Tom Dauncey | PAN-021438 | Yes - Settled Storm (AC0094702) | Yes - U_MON3&4 for SS Permit AC0094702 | 811.6 | No | Crickhowell STW, Abergavenny Rd, Crickhowell, NP8 1ED | River Usk | SO 22506 17473 | SO 22513 17473 | SO 22484 17543 | SO 22513 17495 | SO 22481 17544 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 25mg/l NH3. Maximum Limits: 80 mg/l BOD, 54 mg/l NH3. | N/A | Yes | Permits_drawings_1_AC0094701 | N/A | 5mg/l - Current samples show P concentration cannot meet backstop, investment is required. Cannot accept backstop immediately. | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | AC0094702 | Yes | SO 22485 17479 | SO 22494 17504 | SO 22523 17511 | 21 l/s | 222 | Off-line | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LITTLE MILL STW MONKSWOOD USK | AD0002501 | Helen Johns | PAN-021565 | No | Yes - U_Mon3&4 | 82 | No | Little Mill STW, Monkswood, Berthin Brook | River Usk | SO 33771 02390 | SO 33771 02390 | N/A | N/A | SO 33734 02394 | LuT (95%ile) Limits: 55mg/l BOD, 55mg/l SS, pH value 6-9 (maximum range). | N/A | Yes | Permits_drawings_1_AD0002501 | N/A | 5mg/l - insufficient samples to accept backstop immediately (samples collected by October 23) | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANDOVERY WASTEWATER TREATMENT | BN0202701 | Helen Johns | PAN-021355 | Yes - Settled Storm (BN0202702) | Yes - U_MON3&4 for SS Permit BN0202702 | 705 | No | Llandovery WwTW, Llandovery, Carmarthenshire | Afon Bran | SN 76130 33180 | SN 76128 33167 | N/A | N/A | SN 76130 33166 | LuT (95%ile) Limits: 18mg/l BOD, 31mg/l SS, 5mg/l NH3. Maximum Limits: 54mg/l BOD, 20 mg/l NH3. | N/A | Yes | Permits_drawings_1_BN0202701 | N/A | 5mg/l - can accept backstop immediately | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | BN0202702 | Yes | SN 76117 33173 | SN 76135 33149 | SN 76130 33180 | 20.5l/s | 150 | Off-line | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ADPAR WWTW ADPAR CEREDIGION | BN0112801 | Helen Johns | PAN-021284 | Yes - Settled Storm (BP0350601) | Yes - U_MON3&4 for SS Permit BP0350601 | 535 | No | Adpar WwTW, Newcastle Emlyn, Ceredigion | Afon Teifi | SN 30496 40814 | SN 30470 41004 | N/A | N/A | SN 30496 40814 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS. Maximum Limits: 80mg/l BOD. | N/A | Yes | Permits_drawings_1_BN0112801 | N/A | 5mg/l - insufficient samples to accept backstop immediately (samples collected by October 23) | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | BP0350601 | Yes | SN 30496 40814 | SN 30466 41016 | SN 30463 41017 | 18l/s | 150 | Off-line | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LAMPETER STW LAMPETER | BP0045001 | Tom Dauncey | PAN-021498 | Yes - Storm (BP0045002) | Yes - U_MON3&4 for Storm Permit BP0045002 | 1201 | No | Lampeter STW, Lampeter | River Teifi | SN 57630 47340 | SN 57562 47540 | SN 57598 47572 | SN 57562 47540 | SN 57602 47576 | LuT (95%ile) Limits: 100mg/l BOD, 100mg/l SS. | N/A | Yes | Permits_drawings_1_BP0045001 | N/A | 0.5mg/l - 31/03/2025 start date | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | BP0045002 | Yes | SN 57630 47340 | SN 57572 47545 | SN 57572 47545 | 90l/s | No | No | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CILGERRAN STW | BP0217801 | Helen Johns | PAN-021277 | Yes - Settled Storm (BP0217802) | Yes - U_MON3&4 for SS Permit BP0217802 | 408 | No | Cilgerran STW, Cilgerran | River Teifi | SN 19480 43240 | SN 19392 43175 | N/A | N/A | SN 19392 43175 | LuT 95%ile) Limits: 50mg/l BOD, 60mg/l SS, 25mg/l NH3. Maximum Limits: 100mg/l BOD, 54 mg/l NH3. | N/A | Yes | Permits_drawings1_BP0217801 | N/A | 5mg/l - can accept backstop immediately | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A (See Settled Storm) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | BP0217802 | Yes | SN 19480 43240 | SN 19390 43203 | SN 19401 43202 | 9.4l/s | 69 | Off-line | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CORWEN WWTW FINAL EFFLUENT | CM0018301 | Emma Dulson | PAN-021280 | Yes - Settled Storm (CM0018302) | Yes - U_MON3&4 for SS Permit CM0018302 | 716.1 | Yes | Corwen WwTW, Corwen, Denbighshire, LL21 0DN | River Dee | SJ 08276 43573 | SJ 08204 43621 | N/A | N/A | SJ 08190 43600 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 25mg/l NH3. Maximum Limits: 80mg/l BOD, 120mg/l SS, 54mg/l NH3. | Limit of Specified Activity: The discharge derives from an agglomeration with a population equivalent of less than 2,000 discharging to freshwater. | No | Permits_drawings1_CM0018301 | N/A | 1mg/l - 31/03/2030 start date | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | CM0018302 | Yes | SJ 08276 43573 | SJ 08151 43614 | SJ 08184 43590 | 14.85l/s | 192 | Off-line | No greater than 10mm in more than 2 dimension | 10mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CLYNDERWEN STW | BG0029501 | Emma Dulson | PAN-021279 | Yes - Storm (BP0324401) | Yes - U_MON3&4 for Storm Permit BP0324401 | 182.8 | Yes | Clynderwen STW, Clynderwen, Pembrokeshire, SA66 7HB | Pont Shan Brook | SN 12390 18320 | SN 12364 18348 | N/A | N/A | SN 12350 18341 | LuT (95%ile) Limits: 13mg/l BOD, 17mg/l SS, 3.5mg/l NH3. | N/A | No | Permits_drawings1_BG0029501 | N/A | 0.25mg/l - 31/03/2032 start date | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | BP0324401 | Yes | SN 12386 18320 | SN 12355 18390 | SN 12365 18381 | 20l/s | No | No | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
WOLFSCASTLE STW | BH0068601 | Emma Dulson | PAN-021633 | Yes - Storm (BG0011602) | Yes - U_MON3&4 for Storm Permit BG0011602 | 77.3 - application has been submitted to increase to 150m3 | No | Wolfscastle STW, Wolfscastle | Afon Anghof | SM 95851 26626 | SM 95825 26635 | N/A | N/A | SM 95827 26636 | LuT (95%ile) 55mg/l BOD, 66mg/l SS, 14.1mg/l NH3. Proposed in submitted application: LuT (95%ile) Limits: 26.5mg/l BOD, 39.5mg/l SS. | N/A | Yes | Permits_drawings_1_BH0068601 | N/A | 4.5mg/l / 2.3mg/l (if growth to 150m3 DWF applied from application confirmed) - 31/03/2025 start date | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | BG0011602 | Yes | SM 95851 26626 | SM 95816 26654 | SM 95800 26644 | 10.4l/s | No | No | No | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LETTERSTON WEST STW | BH0071101 | Helen Johns | PAN-021352 | Yes - Storm (BH0071102) | Yes - U_MON3&4 for Storm Permit BH0071102 | 510 | No | Letterston West WwTW, Letterston, Pembrokeshire, SA62 5TU | Western Cleddau | SM 92870 29020 | SM 93440 29450 | N/A | N/A | SM 93444 29463 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS, 20mg/l NH3. | N/A | Yes | Permits_drawings_1_BH0071101 | N/A | 2.5mg/l - 31/03/2025 start date | N/A | N/A | Please see U_MON3/4 information provided by Mathew Griffiths | BH0071102 | Yes | SM 93009 29075 | SM 93447 29464 | SM 93498 29468 | 24.3l/s | No | No | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Note on AS2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Will be N/A for all.
Note on AX7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Emergency activity removed in error in the 2020 variation.