Notice of request for more information

Environmental Permitting (England and Wales) Regulations 2016

Notice requiring further information

To:

Mono Metals Limited,

Agincourt House,

14 Clytha Park Road,

Newport,

Gwent,

Wales.

NP20 4PB

Application number: PAN-021065

Natural Resources Wales, in exercise of its powers under paragraph 4 of Part 1 of Schedule 5 of the above Regulations, requires you to provide the information detailed in the attached schedule. The information is required in order to determine your application for a permit, dated 20/10/2023.

The information requested should be sent to the following email address by 02/02/2024.

Information should be sent to bryan.burn@naturalresourceswales.gov.uk

| Name | Date |
| --- | --- |
| Bryan Burn | 19/01/2024 |

Authorised on behalf of Natural Resources Wales

Schedule

Fire prevention and mitigation plan

The questions in this section are about the following Fire Prevention and Mitigation Plan (FPMP) provided in the application – ECCS 145 001 R 003 B FPMP Final, Dated October 2023. This is the document we are referring to in the questions below when we refer to ‘your FPMP’, or ‘your Fire Prevention and Mitigation Plan’.

Within the questions below when we say ‘our FPMP guidance’ we are referring to Guidance Note 16. Fire Prevention and Mitigation Plan Guidance – Waste Management (Version 2, 2017). A link to this document is below.

Guidance No. 16 Fire prevention and mitigation plan - waste management (naturalresources.wales)

Within the questions below we also refer to your Environmental Risk Assessment provided in the application – ECCS 145 001 R 001 B OTMP Final, dated October 2023. This is the document we are referring to when we refer to ‘your OTMP’.

Within the questions below we also refer to your Operational Techniques & EMS Summary Report provided in the application – ECCS 145 001 R 002 B ERA Final, dated October 2023. This is the document we are referring to when we refer to ‘your ERA’.

- ACTION: Confirm the number of storage containers which will be located within the bund in the external working area and the types of wastes stored therein and update your FPMP (including site layout plan if necessary) to ensure that all information is consistent.

- Section 4.6 of your FPMP – states ‘There are 3 x 1,000litre tanks contained within the bund One for the storage of diesel, another for gas oil, and the third will contain lubricant oils.’.

- Your site layout plan in Appendix B of your FPMP shows 2x fuel oil storage tanks and 2x waste oil tanks with an additional antifreeze storage tank.

- Table 4.4.1 of your FPMP indicates 1x diesel, 1x gas oil and 1x lubricating oil. You do not identify storage for petrol although we understand that fuels may be mixed in storage containers.

- Section 6.7 point 3 of your FPMP states there will be 5 tanks, this aligns with your site layout plan and states ‘These will include waste fuel tanks (hydraulic oils & brake fluid oils), anti-freeze liquid tank, and fuel oil tanks (diesel & petrol).’ This is also referred to in your OTMP section 2.1.1 and your ERA section 2.6.1.

- ACTION: Update your site plan to show the location of all waste material storage.

- Your site layout plan in Appendix B of your FPMP does not show the location of a number of waste storage locations.

- Section 4.5 of your FPMP states ‘Any lubricants / grease stored on site for maintenance of equipment will be held within a secure containers and stored > 6 metres distance from any waste stockpile.’ This storage is not shown on the site layout plan in Appendix B of your FPMP.

- Section 2.1.3 of your OTMP refers to ‘uncontaminated plastics, glass and ferrous and non-ferrous metal wastes arising from the depolluting activities’. Plastic and glass do not have an identified storage location on the site layout plan in your FPMP appendix B.

- Section 2.1.4 of your OTMP refers to liquified gas tanks. This waste is not mentioned elsewhere and no storage is identified on the site layout plan in Appendix B of your FPMP. This section also refers to components containing magnesium and mercury. The protocols and locations for storage of these are not identified.

- ACTION: Update Section 1.3 of your FPMP and Section 1.1.2 of your OTMP to correct your stated distance from the nearest residential property.

  - Section 1.3 of your FPMP, and Section 1.1.2 of your OTMP state ‘The nearest residential properties are along Milman Street (70m West of the Site).’ This was raised with you in point 6a of our request for information and whilst you have amended your table 1.4.1 in your FPMP and table 1.11.1 of your OTMP you have not amended Section 1.3 of your FPMP or Section 1.1.2 of your OTMP.

- ACTION: Update Section 1.9 of your FPMP, Section 1.6 of your ERA and Section 1.5 of your OTMP to correct your statement that ‘there are no point source emissions proposed from the waste operations’ to identify that there is a point source emission to sewer.

  - In your response to point 4a of our request for information you updated Form B4 and amended Section 2.6 of your ERA, but you have not updated all relevant sections of your FPMP, ERA and OTMP.

- ACTION: Update your FPMP to confirm the maximum storage per waste stream on your site.

- Section 4.4 table 4.4.1 of your FPMP – not all of your maximum storage sizes are correct, your calculations and dimensions for your storage are confusing and/or inaccurate.

- Section 4.1 of your FPMP states ‘No more than 25 tonnes of intact waste vehicle tyres (waste code 16 01 03) shall be stored at the site.’ However, table 4.4.1 of your FPMP indicates that the maximum volume to be stored as 0.6tonnes.

- ACTION: Provide the product technical specifications for the materials used for the quarantine area walls and confirm that the installation method of the products used is in line with the manufacturers recommended installation requirements.

  - Section 4.1 of your FPMP states that ‘The site will have a dedicated quarantine area situated in the outside yard area, which will be walled and located at least 6m away from all other waste storage areas.’ Section 11 of our FPMP guidance requires that the bays and/or walls should be able to provide 120 minutes fire resistance period and that the product specification will need to be established via approved stockiest to ensure appropriate standard of fire resistance are met. It is essential that when installing such products that the installation method used is in line with the manufacturers recommended installation requirements.

- ACTION: Update your FPMP to address all of the points in Section 11 -Enclosing stacks using bays and walls, of our FPMP guidance.

  - Appendix F – FPMP Checklist in your FPMP notes N/A in reference to Section 11 of our FPMP guidance. This is incorrect, as identified in point 6 above your quarantine bay is walled to 3 sides.

- ACTION: Update your FPMP to provide accurate calculations for the total floor space for the building and the firewater retention capacity for both the building and the outside yard. Also confirm the height of the ‘sleeping policemen’ at the entrance points. These figures should also be updated in your OTMP Section 2.1.1 and your Environmental Risk Assessment Section 2.6.1.

  - Section 6.7 of your FPMP gives the building dimensions as 59x23m with a total floor space of 1587m2, this total is inaccurate. Section 6.7 of your FPMP also refers to the addition of 12” (30cm) sleeping policemen at the entrance points to the building and you suggest a fire water retention capacity of 413m3, again this figure is inaccurate and it does not take into account the footprint of storage containers, wastes or the 20,000ltr water tank.

  - Section 6.7 of your FPMP gives the outside yard dimensions and total floor space which calculate correctly although your given fire water retention capacity of 557m3 is inaccurate and does not take into account buildings, waste storage including the hazardous liquids bund, or the capacity of the drainage system and interceptor.

  - Section 6.7 and Appendix B of your FPMP refer to ‘12” sleeping policemen’. If this height is inaccurate then the fire water retention capacities will also be inaccurate.

- ACTION: Update Section 2.1 of your OTMP to align with the maximum storage times for wastes stated in Section 4.2 of your FPMP.

  - Section 2.1 of your OTMP states ‘Wastes shall not be stored for longer than 1 year prior to disposal, and 3 years prior to recovery.’ Section 4.2 of your FPMP indicates maximum storage times of 3 and 6 months.

- ACTION: Update Section 2.1.2 of your OTMP to clarify the capacity of the quarantine area to ensure that it is consistent with the information within the FPMP.

  - Section 2.1.2 of your OTMP states ‘The quarantine area will be capable of holding a minimum of 6m3 of material (which is 50% of the largest stockpile of material proposed).’. Section 4.4 of your FPMP identifies the largest storage size as 50m3 which would require a minimum capacity of 25m3.

- ACTION: Update your FPMP to include procedures used to ensure that your quarantine area will be cleared of non-conforming waste prior to using the quarantine area in the event of a fire.

  - Section 2.1.2 of your OTMP states ‘The Facility will have a quarantine area for the temporary storage of any non-conforming or contamination removed from waste deliveries.’

  - Section 6.8 of your FPMP does not describe how you will ensure the quarantine area will be cleared of non-conforming wastes in the event of a fire on site prior to using the quarantine area being used to deposit wastes in the event of a fire. Your application, OTMP, FPMP and site plans show only one quarantine area.

  - Section 22 – Designated quarantine area – of our FPMP guidance states: ‘You should keep at least one specified quarantine area clear at all times – unless it is being used in the event of a fire. If you use your quarantine area to store material temporarily (for example, non-permitted wastes) you should make sure you can remove those wastes as soon as is practicable. In the event of a fire, you must remove those wastes immediately. Your FPMP should include details of the procedure you will use to do this.’