| Gower Lodge (Swansea) Ltd Orbis Education and Care Ltd Vision Court Caxton Place Cardiff CF23 8HA | Ein cyf / Our ref: BP0316301 Ty Seren 190724 Eich cyf / Your ref: Dyddiad/Date: 24 July 2019 |
| --- | --- |

Dear Sir/Madam

TY SEREN, CEFN STYLLE ROAD, GOWERTON, SWANSEA

On 3rd July 2019 a sample taken of the discharge from the sewage treatment works at Ty Seren failed Condition 1.6 of the EPR Water Discharge Permit BP0316301. The failures are as follow:

- Biological Oxygen Demand (BOD) was 50.9 mg/l with a permitted limit of 20 mg/l

- Ammonia was 28.3 mg/l with a permitted limit of 20mg/l

These results are worse than the previous sample taken in January 2019.

Suspended solids are also monitored, but did not breach the limits with a result of 22.5 mg/l with a permitted limit of 30mg/l.

We are aware that there were issues with the package plant last year, but my understanding is that those issues were resolved some time ago, so I would expect the discharge quality to be reaching the required quality by now.

Please can you explain in writing, before 12th August 2019, the reason(s) for this failure and the measures you will be taking to ensure that, in the future, the discharge from the sewage treatment works at Ty Seren is compliant with the conditions of the permit.

When we have received your explanation, we will be writing a Compliance Assessment Report which we will send on to you for review before publishing it on our Public Register.

Please ensure that the person responding on behalf of Gower Lodge (Swansea) Ltd is authorised or has been authorised to respond on behalf of the company and that this is also stated in the response.

# If you have any other queries please do not hesitate to contact me, my details are below.

Yours sincerely

Sarah Bennett

Officer

# Deialu uniongyrchol/Direct dial 0300 065 3205

E-bost uniongyrchol/Direct e-mail sarah.bennett@cyfoethnaturiolcymru.gov.uk