## Flow Split Calculations
Erw Faethlon Hydro Intake Notches for HOF of Q95 + 30% Residual Flow
Hands Off Flow (HOF) notch
Level relative to screen notch |  | -0.05 | m |  | Hands Off Flow (Q95) |  | 2 | l/s
Elevation |  | 154.95 | m AOD |  | Residual above HOF |  | 30%
Width |  | 0.07 | m |  | Min Turbine Flow |  | 1.5 | l/s
Discharge co-efficient |  | 1.6 | Broad crested |  | Max Turbine Flow |  | 15 | l/s
Residual flow notch |  |  |  |  | Screen Notch (flow to turbine)
Level relative to Screen notch |  | -0.01 | m |  | Level |  | 0 | m (datum level)
Elevation |  | 154.99 | m AOD |  | Elevation |  | 155 | m AOD
Width |  | 0.095 | m |  | Width |  | 0.51 | m
Discharge co-efficient |  | 1.6 | Broad Crested |  | Discharge Coefficient |  | 1.55 | Coanda on broad crest Cd
Width of Residual + HOF notches |  | 0.165 | m
Notch Flow = Width x Discharge Coefficient x Level^1.5
Q95 +30%
Level above screen notch | Flow in screen notch | Level above HOF notch | Flow in HOF notch | Level above residual notch | Flow in residual notch | Total flow | Turbine Flow | Total residual flow | Target residual flow | % residual above HOF
m | l/s | m | l/s | m | l/s | l/s | l/s | l/s | l/s
0 | 0 | 0.05 | 1.2522 | 0.01 | 0.152 | 1.4042 | 0 | 1.4042 | 1.4042 | 100%
0.01 | 0.7905 | 0.06 | 1.6461 | 0.02 | 0.42992 | 2.8665 | 0 | 2.8665 | 2.2599 | 100%
0.02 | 2.2359 | 0.07 | 2.0743 | 0.03 | 0.78982 | 5.1 | 2.2359 | 2.8641 | 2.93 | 27.87%
0.03 | 4.1076 | 0.08 | 2.5343 | 0.04 | 1.216 | 7.8578 | 4.1076 | 3.7503 | 3.7573 | 29.88%
0.04 | 6.324 | 0.09 | 3.024 | 0.05 | 1.6994 | 11.0474 | 6.324 | 4.7234 | 4.7142 | 30.1%
0.05 | 8.8381 | 0.1 | 3.5418 | 0.06 | 2.2339 | 14.6137 | 8.8381 | 5.7757 | 5.7841 | 29.93%
0.06 | 11.6179 | 0.11 | 4.0861 | 0.07 | 2.8151 | 18.5191 | 11.6179 | 6.9012 | 6.9557 | 29.67%
0.07 | 14.6403 | 0.12 | 4.6558 | 0.08 | 3.4394 | 22.7354 | 14.6403 | 8.0951 | 8.2206 | 29.39%
0.08 | 17.887 | 0.13 | 5.2497 | 0.09 | 4.104 | 27.2407 | 15 | 12.2407 | 9.5722 | 40.57%
0.09 | 21.3435 | 0.14 | 5.8669 | 0.1 | 4.8067 | 32.0171 | 15 | 17.0171 | 11.0051 | 50.03%
0.1 | 24.9978 | 0.15 | 6.5066 | 0.11 | 5.5454 | 37.0498 | 15 | 22.0498 | 12.5149 | 57.2%
0.11 | 28.8397 | 0.16 | 7.168 | 0.12 | 6.3185 | 42.3262 | 15 | 27.3262 | 14.0979 | 62.8%
0.12 | 32.8605 | 0.17 | 7.8504 | 0.13 | 7.1246 | 47.8354 | 15 | 32.8354 | 15.7506 | 67.27%
0.13 | 37.0524 | 0.18 | 8.5532 | 0.14 | 7.9622 | 53.5679 | 15 | 38.5679 | 17.4704 | 70.91%
0.14 | 41.4089 | 0.19 | 9.2757 | 0.15 | 8.8304 | 59.5151 | 15 | 44.5151 | 19.2545 | 73.92%
0.15 | 45.9239 | 0.2 | 10.0176 | 0.16 | 9.728 | 65.6695 | 15 | 50.6695 | 21.1008 | 76.44%

## Flow Modelling
Low-Flow Estimates from LowFlows
www.hydrosolutions.co.uk
Catchment Characteristics
Region | England: | Wales
Area | (64) | Dyfi
Boundary source | Imported Polygon
Catchment Area | km2 | 0.752 | This is based on lower down as LF was struggling with the small catchment
No significant lakes in catchment
Grid resolution used for derivation of catchment characteristics | m | 20
Runoff | (mm) | 795.1
BFI | 0.442
Catchment at actual intake site | 0.598 | km2 | to scale
| From LF | Scaled for this project
Qmean | 0.019 | 0.015109
Q(0.1) | 0.211 | 0.16779
Q(1) | 0.114 | 0.090654
Q(2) | 0.09 | 0.071569
Q(3) | 0.076 | 0.060436
Q(4) | 0.067 | 0.053279
Q(5) | 0.061 | 0.048508
Q(6) | 0.056 | 0.044532
Q(7) | 0.051 | 0.040556
Q(8) | 0.048 | 0.03817
Q(9) | 0.045 | 0.035785
Q(10) | 0.043 | 0.034194
Q(11) | 0.04 | 0.031809
Q(12) | 0.038 | 0.030218
Q(13) | 0.036 | 0.028628
Q(14) | 0.035 | 0.027832
Q(15) | 0.033 | 0.026242
Q(16) | 0.032 | 0.025447
Q(17) | 0.03 | 0.023856
Q(18) | 0.029 | 0.023061
Q(19) | 0.028 | 0.022266
Q(20) | 0.027 | 0.021471
Q(21) | 0.026 | 0.020676
Q(22) | 0.025 | 0.01988
Q(23) | 0.025 | 0.01988
Q(24) | 0.024 | 0.019085
Q(25) | 0.023 | 0.01829
Q(26) | 0.022 | 0.017495
Q(27) | 0.022 | 0.017495
Q(28) | 0.021 | 0.016699
Q(29) | 0.02 | 0.015904
Q(30) | 0.02 | 0.015904
Q(31) | 0.019 | 0.015109
Q(32) | 0.019 | 0.015109
Q(33) | 0.018 | 0.014314
Q(34) | 0.018 | 0.014314
Q(35) | 0.017 | 0.013519
Q(36) | 0.017 | 0.013519
Q(37) | 0.016 | 0.012723
Q(38) | 0.016 | 0.012723
Q(39) | 0.015 | 0.011928
Q(40) | 0.015 | 0.011928
Q(41) | 0.014 | 0.011133
Q(42) | 0.014 | 0.011133
Q(43) | 0.014 | 0.011133
Q(44) | 0.013 | 0.010338
Q(45) | 0.013 | 0.010338
Q(46) | 0.013 | 0.010338
Q(47) | 0.012 | 0.0095426
Q(48) | 0.012 | 0.0095426
Q(49) | 0.012 | 0.0095426
Q(50) | 0.011 | 0.0087473
Q(51) | 0.011 | 0.0087473
Q(52) | 0.011 | 0.0087473
Q(53) | 0.011 | 0.0087473
Q(54) | 0.01 | 0.0079521
Q(55) | 0.01 | 0.0079521
Q(56) | 0.01 | 0.0079521
Q(57) | 0.01 | 0.0079521
Q(58) | 0.009 | 0.0071569 | 58
Q(59) | 0.009 | 0.0071569 | 59
Q(60) | 0.009 | 0.0071569 | 60
Q(61) | 0.009 | 0.0071569 | 61
Q(62) | 0.008 | 0.0063617 | 62
Q(63) | 0.008 | 0.0063617 | 63
Q(64) | 0.008 | 0.0063617 | 64
Q(65) | 0.008 | 0.0063617 | 65
Q(66) | 0.008 | 0.0063617 | 66
Q(67) | 0.007 | 0.0055665 | 67
Q(68) | 0.007 | 0.0055665 | 68
Q(69) | 0.007 | 0.0055665 | 69
Q(70) | 0.007 | 0.0055665 | 70
Q(71) | 0.007 | 0.0055665 | 71
Q(72) | 0.006 | 0.0047713 | 72
Q(73) | 0.006 | 0.0047713 | 73
Q(74) | 0.006 | 0.0047713 | 74
Q(75) | 0.006 | 0.0047713 | 75
Q(76) | 0.006 | 0.0047713 | 76
Q(77) | 0.006 | 0.0047713 | 77
Q(78) | 0.005 | 0.0039761 | 78
Q(79) | 0.005 | 0.0039761 | 79
Q(80) | 0.005 | 0.0039761 | 80
Q(81) | 0.005 | 0.0039761 | 81
Q(82) | 0.005 | 0.0039761 | 82
Q(83) | 0.005 | 0.0039761 | 83
Q(84) | 0.004 | 0.0031809 | 84
Q(85) | 0.004 | 0.0031809 | 85
Q(86) | 0.004 | 0.0031809 | 86
Q(87) | 0.004 | 0.0031809 | 87
Q(88) | 0.004 | 0.0031809 | 88
Q(89) | 0.004 | 0.0031809 | 89
Q(90) | 0.003 | 0.0023856 | 90
Q(91) | 0.003 | 0.0023856 | 91
Q(92) | 0.003 | 0.0023856 | 92
Q(93) | 0.003 | 0.0023856 | 93
Q(94) | 0.003 | 0.0023856 | 94
Q(95) | 0.003 | 0.0023856 | 95
Q(96) | 0.003 | 0.0023856 | 96
Q(97) | 0.002 | 0.0015904 | 97 | Interpolating to find Q95 by using trendline on graph below
Q(98) | 0.002 | 0.0015904 | 98 |  | m | C | x | Q95
Q(99) | 0.002 | 0.0015904 | 99 | linear trendline | -0.00013934 | 0.015242 | 95 | 0.0020053
Q(99.9) | 0.001 | 0.00079521 | 99.9