Permit Number: 	BP3135EB						Operator: 	Sensient Flavors and Volac International Limited

Facility:		Felinfach Effluent Treatment Plant		Form Number: 	Water1 / 17/08/2022

# Reporting of emissions to water for the period from 01/01/2023 to 31/12/2023

| Emission Point | Substance / Parameter | Emission # Limit Value | Reference Period | Result [1] | Test Method [2] | Sample Date and Times [3] | Uncertainty [4] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| W1 | Total volume of treated effluent | 2,750 m3/day | 24 hour | 2029 | MCERTS self-monitoring of effluent flow scheme | 01/01/2023 | 99% |
|  | Maximum flow rate | 37 l/s | instantaneous | 24l/s |  |  |  |
|  | pH range | 6-9 | instantaneous | 6.72 – 8.79 |  |  | 99% |
|  | Chemical oxygen demand (COD) | 180 mg/l | 24 hr composite | 171mgl | As per the Environmental Agency’s Technical Guidance M18 Monitoring of discharges to water and sewer | 07/ 06/2023 | 98% |
|  | Biological oxygen demand (BOD) | 100 mg/l | 24 hr composite | 5.25mg/l |  |  |  |
|  | Total suspended solids | 60 mg/l | 24 hr composite | 59mg/l |  | 19/01/2023 |  |
|  | Colour (platinum – cobalt scale) | No limit set (Hazen units) | 24 hr composite | 6.64 max | Colorimetric analysis at 400nm | 16/02/2023 | 99% |
|  | Total ammonia | No limit set | 24 hr composite | 5.76mg/l | As per the Environmental Agency’s Technical Guidance M18 Monitoring of discharges to water and sewer | 04/10/2023 |  |
|  | Total nitrogen (Total N) | 25 mg/l | 24 hr composite | 15.25mg/l |  | 04/10/2023 |  |
|  | Total phosphorus (Total P) | 2 mg/l | 24 hr composite | 3.1 |  | 28/07/2023 |  |

- The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

- Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.

- For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.

- The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

Signed ……Byron Williams……………………………………………………….  		Date……30/01/2024…………………..

(Authorised to sign as representative of Operator)

COMMENTS

Over the year has process has been very stable with all parameters met except for Phosphate which recorded 3.1mg/l against a limit of 2.0mg/l. However, the average phosphate over all samples was 1.3mg/l. This level has been achieved by the upgrade of the aeration system towards the end of 2022, this has enabled the biological process to limit the phosphate levels naturally without the need of addition of any chemicals.

Treated water volume discharge maximum recorded was 2029 m3 per day The actual average was 1494m3 with an average of 650m3 recycled as potable water to the factory.

Permit Number: 	BP3135EB						Operator: 	Sensient Flavors and Volac International Limited

Facility:		Felinfach Effluent Treatment Plant		Form Number: 	WaterUsage1 / 17/08/2022

# Reporting of Water Usage for the year 2023

| Water Source | Usage (m3/year | Specific Usage (m3/unit output) |  |
| --- | --- | --- | --- |
| Mains water | 90 |  |  |
| Site borehole | 1984 |  |  |
| River abstraction |  |  |  |
| TOTAL WATER USAGE | 2074 |  |  |

Operator’s comments :

Signed …………Byron Williams………………………………………………….  		Date………30/1/2024………………..

(authorised to sign as representative of Operator)

Permit Number: 	BP3135EB						Operator: 	Sensient Flavors and Volac International Limited

Facility:		Felinfach Effluent Treatment Plant		Form Number: 	Energy1 / 17/08/2022

# Reporting of Energy Usage for the year 2023

| Energy Source | Energy Usage |  | Specific Usage (MWh/unit output) |  |
| --- | --- | --- | --- | --- |
|  | Quantity | Primary Energy (MWh) |  |  |
| Electricity * | MWh | 1925 |  |  |
| Natural Gas | MWh |  |  |  |
| Gas Oil | tonnes |  |  |  |
| Recovered Fuel Oil | tonnes |  |  |  |
| TOTAL | - | 1925 |  |  |

* Conversion factor for delivered electricity to primary energy = 2.4

Operator’s comments : Continued maintenance of the aeration systems has shown a drop of in consumption of 46% on the year 2022

Signed ………Byron Williams…………………………………………………….  		Date……30/1/2024…………………..

(Authorised to sign as representative of Operator)

Permit Number: 	BP3135EB						Operator: 	Sensient Flavors and Volac International Limited

Facility:		Felinfach Effluent Treatment Plant		Form Number: 	Performance1 / 17/08/2022

# Reporting of other performance indicators for the period 01/01/2023 to 01/12/2023

| Parameter |  | Units |  |
| --- | --- | --- | --- |
| Treated liquid effluent discharged at W1 |  | 507302 m3 |  |
| Sludge collected for off-site recovery |  | 38810 m3 |  |
| Sodium Hydroxide used |  | 468 tonnes |  |
| Generation of residues |  | tonnes |  |
| Generation of waste water |  | m3 |  |

Operator’s comments :

Signed ………………Byron Williams…………………………………………….  		Date……30/01/2024…………………..

(Authorised to sign as representative of Operator)