Permit Number: 	AB3233DW					Operator: 		GP Services Ltd

Facility:		Great Porthamel Farm AD Plant		Form Number: 	 Air1 - 12/03/12
Reporting of emissions to air for the period from 11/06/2015 to 16/11/2016 
	Emission
Point
	Substance /
Parameter
	Emission
Limit Value
	Reference Period
	Result [1]
	Test
Method [2]
	Sample
Date and Times [3]
	Uncertainty
[4]

	A1
	Oxides of nitrogen 
	500 mg/m3
	Hourly Mean
	381
	BS EN 14792: 2005
	16/11/2016
10.55-11.55
	

	
	Carbon  monoxide
	1400 mg/m3
	Hourly Mean
	936
	BS EN 15058: 2006
	16/11/2016
10.55-11.55
	

	
	Sulphur dioxide
	350 mg/m3
	Hourly Mean
	1.5
	BS EN 14791: 2005
	16/11/2016
10.55-11.55
	

	
	Total VOCs including methane
	1000 mg/m3
	Hourly Mean
	794
	BS EN 12616: 1999; BS EN 13526: 2002
	16/11/2016
10.55-11.55
	

	A2
	Oxides of Nitrogen
	500 mg/m3
	Hourly Mean
	431
	BS EN 14792: 2005
	16/11/2016
12.25-13.25
	

	
	Carbon  monoxide
	1400 mg/m3
	Hourly Mean
	610
	BS EN 15058: 2006
	16/11/2016
12.25-13.25
	

	
	Sulphur dioxide
	350 mg/m3
	Hourly Mean
	0.35
	BS EN 14791: 2005
	16/11/2016
12.25-13.25
	

	
	Total VOCs including methane
	1000 mg/m3
	Hourly Mean 
	555
	BS EN 12616: 1999; BS EN 13526: 2002
	16/11/2016
12.25-13.25
	

	Emergency Flare1
	Oxides of Nitrogen
	No limit set


	None specified

	
	None specified
	
	

	
	Carbon  monoxide
	
	
	
	
	
	

	
	Total VOCs including methane
	
	
	
	
	
	




1Annual monitoring is only required when flare operates in excess of 10% of the time, taken on an annual assessment period.
The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.
Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Environment Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.
For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   
The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.



Signed …………L Warry………………………………………………….  		Date………1 March 2017………………..   	
	(Authorised to sign as representative of Operator)
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