
	CONSENT NO.   
	BG0007805


WATER RESOURCES ACT 1991
SECTION 88 ‑ SCHEDULE 10

(AS AMENDED BY THE ENVIRONMENT ACT 1995)
VARIATION OF CONSENT TO DISCHARGE
TO:
Environment Quality Scientist


Dŵr Cymru Cyfyngedig

Pentwyn Road


Nelson

Treharris

CF46 6LY

	In pursuance of an application by the consent holder for variation of consent, the ENVIRONMENT AGENCY ("The Agency") in pursuance of its powers under the Water Resources Act 1991 HEREBY VARIES ITS CONSENT to the making of a discharge OF SEWAGE EFFLUENT, as follows:

Settled Storm Sewage

With respect to Consent No. BG0007805 issued on the 13th day of December 1991

	FROM: Pencader Sewage Treatment Works storm tanks.

	AT: Pencader, Camarthenshire, SA39 9BS

	TO: The River Ely.

	HEREAFTER SUBJECT TO the conditions set out in the following schedule(s):

   Settled Storm Sewage          Schedule No. BG000780501



	Subject to the provisions of Paragraphs 7 and 8 of Schedule 10 of the Water Resources Act 1991, no notice shall be served by the Agency, which alters the effect of variations made by this consent, without the agreement in writing of the consent holder, during a period of 4 years from the date this variation is issued.

	This variation of consent is issued and takes effect on the 25th day of March 2008
Signed: [image: image1.png]H A Bicher




Mel Bischer – National Permitting Team Leader 




	CONSENT NO.
	BG0007805

	SCHEDULE NO.
	BG000780501

	DATE  ISSUED  
	25 March 2008


CONDITIONS OF CONSENT TO DISCHARGE

Settled Storm Sewage ("the Discharge")

FROM: Penacader Sewage Treatment Works Storm Tanks, Pencader, Camarthenshire. 
NATURE

1.
The Discharge shall consist solely of settled storm sewage.

LOCATION

2.
The Discharge shall be made in the manner and at the place specified as:

(a) 
discharging via a pipe;

(b) 
discharging to the Afon Tyweli;

(c) 
at National Grid Reference SN 44556 36582;

(d) 
shown marked 'Consent Point' on Plan BG0007805 attached as Annex 1.

SAMPLE POINT

3.
A sample point shall be provided and maintained at National Grid Reference SN 44515  36523 as shown marked ‘Sample Point’ on Plan BG0007805, so that a representative sample of the Discharge may be obtained.  The Consent Holder shall ensure that all constituents of the Discharge pass through the said sampling point at all times and in any legal proceedings it shall, for the purposes of Section 10 of the Rivers (Prevention of Pollution) Act 1961, be presumed, until the contrary is shown that any sample of the Discharge taken at the said sampling point is a sample of what was discharging into controlled waters.
VOLUME

4.
The Discharge shall occur when and only for as long as, the storm tanks are full. The discharge of storm sewage to the storm tank shall only occur when the rate of flow at the storm sewage separating weir is in excess of 17.7 litres per second due to rainfall and/or snowmelt. The storm tanks shall be emptied and their contents returned for full treatment as soon as practicable after cessation of the overflow to the storm tanks.

5.
The capacity of the storm tanks shall be at least 88.56 cubic metres.
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COMPOSITION

6.
(a)
The Discharge shall have passed, without prior comminution or maceration, through a screening device having apertures no greater than 6 millimetres in two dimensions.

      
(b)
The screening device shall be maintained in an efficient operational condition.

      
(c)
All screenings must be removed and disposed of in a manner such as to prevent entry to the discharge.

WORKS OPERATION

7.
a)
The works shall be operated and the effluent shall be treated in a manner which, so far as reasonably practicable, minimises the polluting effects of the Discharge made from the works on controlled waters.

b)
This condition does not require any alteration of the works or a change in the type of treatment used.

RECORDING AND REPORTING

8.
(a)
The consent holder shall establish and operate a documented maintenance programme and record all non‑routine actions undertaken that may have adversely affected the operation of the storm tanks. Copies of the programme shall be made available for inspection by the Agency's officers at all reasonable times.

(b) On request the consent holder shall supply the Agency with a written report on the maintenance and all non‑routine actions that may have adversely affected the operation of the storm tanks.

9. The consent holder shall notify the Agency in writing if any known or planned introduction or material change in respect of discharges from trade premises to the sewerage system occurs, that may increase or introduce into the effluent any "dangerous substance" (set out in Annex 2 to this notice as updated from time to time and notified to the consent holder in writing), and any other substance considered by the consent holder as having or likely to have a significant effect on the receiving waters.
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SUBSTANTIAL CHANGE

10.
A discharge shall not be made from the works if it would cause a significant increase in the polluting effects of the Discharge on controlled waters as a result of a new or altered discharge of trade effluent into the works.

11.
A discharge of trade effluent into the works is new if -

(a)
it is made by the sewerage undertaker and is of a kind not made into the works by the undertaker immediately before the date of effect of this variation; or

(b)
it is made by a third party and the discharge is authorised on or after that date.

12.
A discharge of trade effluent into the works is altered if -

(a)
it is made by the sewerage undertaker and its composition or quantity changes significantly on or after the date of effect of this variation; or

(b)
it is made by a third party and the alteration of the discharge is authorised on or after that date.

13.
An increase in the polluting effects of the Discharge on controlled waters is not significant for the purposes of this condition if it relates to any characteristic of the Discharge which is specifically regulated by conditions in this consent but it may be significant if it is caused by a change in some other characteristic of the Discharge.

14.
For the purposes of this condition "trade effluent" means -

(a)
any discharge by the sewerage undertaker other than

(i)
domestic sewage from premises connected directly or indirectly to the works; or

(ii)
surface water run-off;

(b) any discharge by a third party which is authorised under Chapter III of Part IV of the Water Industry Act 1991 or which is accepted as a result of a contract with the sewerage undertaker.
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UNAUTHORISED DISCHARGES 

15.
A Discharge made from the works shall not contain any poisonous, noxious or polluting matter or solid waste matter which is attributable to any unauthorised discharge into the works.

(a)
A Discharge into the works is unauthorised if it is made by a third party and either there is no obligation to receive it or conditions subject to which there is an obligation to receive it are not observed.

(b)
Nothing in this, or any other, condition of this consent prevents anyone from relying on any defence available to them under Section 87 of the Water Resources Act 1991.
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Plan BG0007805
[image: image2.emf]

ANNEX 2

 1.
Mercury and its compounds


2.
Cadmium and its compounds

 3.
Hexachlorocyclohexane (lindane and related compounds)

 4.
Carbon tetrachloride

 5.
DDT (the isomers of 1,1,1‑trichloro‑2,2  bis{p‑chlorophenyl} ethane)

 6.
Pentachlorophenol (PCP)


7.
Aldrin

 8.
Dieldrin




9.
Endrin

10.
Isodrin 




11.
Hexachlorobenzene (HCB)

12.
Hexachlorobutadiene (HCBD)

13.
Chloroform

14.
Polychlorinated biphenyls


15.
Dichlorvos

16.
1,2‑Dichloroethane


17.
Trichlorobenzene

18.
Atrazine




19.
Simazine

20.
Tributyltin compounds


21.
Triphenyltin compounds

22.
Trifluralin



23.
Fenitrothion

24.
Azinphos‑methyl



25.
Malathion

26.
Endosulfan



27.
Lead

28.
Chromium



29.
Zinc

30.
Copper




31.
Nickel

32.
Arsenic




33.
*Iron

34.
*pH outside range 5.5 to 9.0


35.
*Boron

36.
Vanadium



37.
PCSD'S

38.
Cyfluthrin



39.
Sulcofuron

40.
Flucofuron



41.
Permethrin

42.
4-Chloro-3-methyl-phenol


43.
2-Chlorophenol

44.
2,4-Dichlorophenol


45.
2,4-D (ester)

46.
2,4-D (non ester)



47.
1,1,1-Trichloroethane

48.
1,1,2-Trichloroethane


49.
Bentazone

50.
Benzene




51.
Biphenyl

52.
Chloronitrotoluenes


53.
Demeton

54.
Dimethoate



55.
Linuron

56.
MCPA 




57.
Mecoprop

58.
Mevinphos



59.
Napthalene

60.
Omethoate



61.
Toluene

62.
Triazophos



63.
Xylene


64.
Cyanide




65.
Azinphos‑ethyl

66.
Fenthion




67.
Parathion

68.
Parathion‑methyl



69.
Trichloroethylene

70.
Tetrachloroethylene


71.
Dioxins

72.
PAHs 




73.
Nonyl phenol 

74.
Nonyl phenyl ethoxylate 


75.
Di-ethylhexyl phthalate 

76.
Bisphenol-A 



77.
Diazinon 

78.
Chlorfenvinphos 



79.
Chlorotoluron 

80.
Isoproturon



81.
Diuron

82.
Propetamphos 



83.
Flumethrin 

84.
Amitraz 




85.
High-Cis Cypermethrin 

86.
Cyromazine 



87.
Deltamethrin

88.
Cypermethrin  

This list is applicable as at 1 December 1998 and will be updated as and when changes to the relevant legislative requirements occur.

*Notification to the Agency by the Consent holder is only required in respect of changes to trade effluents likely to cause significant changes to the pH value, and/or iron or boron concentrations, of the crude sewage.

Environment Agency , 
PO Box 4209, Sheffield, S9 9BS. Tel   08708 506 506

