# Natural Resources Wales permitting decisions

# Bespoke permit

We have decided to issue the variation for Abbeycwmhir Wastewater Treatment Works operated by Dŵr Cymru Cyfyngedig.

The application number is PAN-020546.

The permit number is AN0178601

The variation is for an amendment of the permit from numeric to descriptive conditions. The National Grid Reference is to be amended to reflect the actual discharge point. In addition, the Dry Weather Flow is to be reduced to 5m3/day to reflect the actual volume being discharged. An improvement condition has also been added to upgrade the current system by 31/03/2028.

The discharge from the works drains into a land drain that discharges to the Clywedog Brook. Most permits with discharge rates of a maximum of 5m3/day are regulated under descriptive conditions. The numeric limits set in 2011 were standard backstop limits that package treatment plants are expected to achieve when regulated under a descriptive permit. Therefore we do not expect a decline in the quality of the effluent by relaxing the permit from numeric to descriptive.

Purpose of this document

This decision document:

- explains how the application has been determined

- provides a record of the decision-making process

- shows how all relevant factors have been taken into account

- justifies the specific conditions in the permit other than those in our generic permit template.

Unless the decision document specifies otherwise we have accepted the applicant’s proposals.

Structure of this document

- Annex 1 the decision checklist

# Annex 1: decision checklist

This checklist should be read in conjunction with the Duly Making checklist.

| ### Aspect | ### Justification / Detail | Criteria met |
| --- | --- | --- |
|  |  | Yes |
| Consultation |  |  |  |
| Scope of consultation | The consultation requirements were identified and implemented. The decision was taken in accordance with RGN 6 High Profile Sites, our Public Participation Statement and our Working Together Agreements. | ü |
| ### Responses to, web publicising | No responses were received. | ü |
| Operator |  |  |  |
| Control of the facility | We are satisfied that the applicant (now the operator) is the person who will have control over the operation of the facility after the grant of the permit. The decision was taken in accordance with EPR RGN 1 Understanding the meaning of operator. | ü |
| European Directives |  |  |  |
| Applicable directives | All applicable European directives have been considered in the determination of the application. | ü |
| WFD | WFD stage 1 screening has been completed and the activity/project have been ruled out as not requiring any further WFD Regulations 2017 assessment. Or, further assessment is not required because there is no conceivable impact pathway to any water body or Protected Area. | ü |
| The site |  |  |  |
| Extent of the site of the facility | The operator has provided a plan which we consider is satisfactory, showing the extent of the site of the facility including discharge points. A plan is included in the permit and the operator is required to carry on the permitted activities within the site boundary. | ü |
| Biodiversity, Heritage, Landscape and Nature Conservation and a designated site under the Wildlife and Countryside Act. | The application is within the relevant distance criteria of a site of heritage, landscape or nature conservation, and/or protected species or habitat . The discharge is 40 metres upstream of the River Ithon SSSI. A Form 1 has been completed which also encompasses this SSSI. A full assessment of the application and its potential to affect the site has been carried out as part of the permitting process. We consider that the application will not affect the features of the site. | ü |
| Habitat Regulation Assessment for a designated site under the EU Habitats Directive | Assessment of Likely Significant Effect: The project has been screened for likelihood of significant effects and, taking account of the advice received from protected sites advisors, is considered not likely to have a significant effect on any Natura 2000/Ramsar site (As documented in section 3.2 of OGN 200 form 1, or section 5 if applicable) | ü |
| Environmental Risk Assessment and operating techniques |  |  |  |
| Environmental risk | We have carried out a risk assessment on behalf of the operator. The operator considers this risk assessment is satisfactory. | ü |
| Operating techniques | We have reviewed the techniques used by the operator and compared these with the relevant guidance notes. The proposed techniques / emission levels for priorities for control are in line with the benchmark levels contained in TGN 7.01 and we consider them to represent appropriate techniques for the facility. | ü |
| The permit conditions |  |  |  |
| Improvement conditions | Based on the information on the application, we consider that we need to impose improvement conditions. We have imposed improvement conditions to ensure that: the current system is upgraded by 31/03/2028. The system will need to be installed by this date in time which is earlier than the NEP delivery date of AMP 8 in 2030. This is to ensure that the discharge will treated sufficiently and comply with AMP8. In addition, we must ensure that these changes address concerns that CADW have. | ü |
| Incorporating the application | We have specified that the applicant must operate the permit in accordance with descriptions in the application, including all additional information received as part of the determination process. These are specified in the Operating Techniques table in the permit. The applicant must ensure that the septic tank is maintained properly including weekly visits to site. This is in line with maintaining a package treatment plant to ensure that that the receiving watercourse is protected as any maintenance problems can be addressed quickly, avoiding potential pollution incidents. | √ |
| Emission limits | We have decided that emission limits should not be set for the parameters listed in the permit. It is considered that a descriptive permit is sufficient to prevent significant deterioration of receiving waters. The dry weather flow is in fact 5m3/day and not 15m/3day as per the original permit. According to OI 01_13 if the discharge volume is less than 5m3/day, unless there are exceptional circumstances, a descriptive permit is sufficient to ensure protection of the receiving watercourse. Although the treatment system consists of a septic tank discharging straight to surface water it has additional biological treatment in the form of a filter bed. The numeric limits set in 2011 had standard backstop limits that package treatment plants are expected to achieve when regulated under a descriptive permit. | ü |
| Considerations of foul sewer | We agree with the operators justification for not connecting to foul sewer. | ü |
| Operator Competence |  |  |  |
| Environment Management System | There is no known reason to consider that the operator will not have the management systems to enable it to comply with the permit conditions. The decision was taken in accordance with RGN 5 on Operator Competence. | ü |
| Sustainable Management of Natural Resources (SMNR) |  |  |
| Considerations of SMNR - Compliance with our General Purpose | We are satisfied that this decision is compatible with our general purpose of pursuing the sustainable management of natural resources in relation to Wales and applying the principles of sustainable management of natural resources” The improvement condition includes a constructed reed bed. | ü |
| Environment Wales Act 2016 |  |  |
| Biodiversity and resilience of ecosystems duty | Section 6 of the Environment Wales Act 2016 requires that we seek to maintain and enhance biodiversity in the exercise of our functions, and in so doing promote the resilience of ecosystems, in a manner that is consistent with the proper exercise of our functions. NRW is satisfied that in this case, we have taken into account and had due regard to this duty in so far as it is consistent with the function of determining an application for a stand alone water discharge activity permit under EPR2016. | ü |