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Reporting of Emissions to Sewer for the period from:	 01.04.2019 to 30.06.2019

	Emission
Point
	Substance /
Parameter
	Emission
Limit Value
	Result [1]
	Test
Method [2]
	Sample
Date and Times [3]
	Accreditation/ Certification [4]
	Uncertainty
[5]

	S1
	pH
	6-11
	Max 10.8
Min 9.0
	Plant & Lab Meters
	09.04.19
29.05.19
	N/A
	N/A

	S1
	Chromium and its compounds
	1 mg/l
	0.82
	Atomic Absorption
	08.05.19
	N/A
	N/A

	S1
	Zinc and its compounds
	2 mg/l
	1.36
	Atomic Absorption
	06.06.19
	N/A
	N/A

	S1
	Nickel and its compounds
	2 mg/l
	0.48
	Atomic Absorption
	04.04.19 & 12.04.19
	N/A
	N/A

	S1
	Total flow
	
	2236 m3
	Ultrasonic Flow Meter at Outfall
	01.04.2019 to 30.06.2019
	M/CERTS
	4.16%



[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.
[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. colorimetry.
[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements, or flow/time proportional samples, the percentage of the process operating time covered by the monitoring is given.   
[4] The accreditation status of the equipment and/or the monitoring organisation, as appropriate, for the methods used for both sampling and analysis.
[5] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated. The following uncertainties are quoted on a different basis (basis as stated) – {The basis of any other uncertainty figure needs to be stated. Where no figure is available the Agency will need to agree an appropriate uncertainty value.} 


Signed …….Philip French  	Date: 05.07.19   (authorised to sign as representative of the Operator)
