## Measuring abstraction quantities

Current abstraction

Dolau House Farm currently has nine chicken sheds which house c.250,000 chickens. Water is supplied to seven of the sheds (c.195,000 chickens) by the three boreholes (BH1 – supplies shed 3; BH 2 - supplies shed 1 and 2; BH 3 – supplies shed 6, 7, 8, and 9), with the remaining two sheds on mains water. The groundwater abstraction is currently not licensed. Groundwater Abstraction is measured and recorded by means of a water meter at each shed.

Groundwater abstraction is recorded by means of a daily water meter reading. The abstraction history is summarised in Table 3.2.

Table 3.2 Summary of abstraction history

| Maximum quantities abstracted |  |  |  |  |
| --- | --- | --- | --- | --- |
| yearly | daily | hourly | peak | max. duration |
| m3/annum | m3/d | m3/hr | l/s | hr/d |
| 12,200 | 75 | Not measured | Unknown | 24 |

At the end of the growing cycle the sheds are washed using groundwater and mains water. This use is not recorded, but is estimated in later sections.

Sitework

In addition, water level loggers were installed into BH1, BH2, and BH3 for 18 days, between 07 July and 24 July 2023. The loggers were installed to cover the peak demand during the end of the growing cycle, as well as the rest period following the growing cycle. Site operations and water consumption (measured daily) during this time are summarised in Table 5.1 and Figure 5.1.

Table 5.1 Site operations and water consumption

| Date range | Site operations | Boreholes used | Average consumption (m3/day) |
| --- | --- | --- | --- |
| 07 - 17 July 2023 | Peak demand | BH1 BH2 BH3 | 8.8 17.1 18.3 Total: 44.1 |
| 18 – 19 July 2023 | Poultry depleted | BH1 BH2 BH3 | 8.1 17.4 11.4 Total: 36.9 |
| 20 – 21 July 2023 | Start of rest period: Washdown of poultry sheds | Mostly BH2 | unknown |
| 22 – 24 July 2023 | Rest period | BH1 and BH3 | Minimal |

Figure 5.1 Daily water consumption

During the site visit on 7 July, instantaneous flow rate from each borehole was estimated. The pipeline from each borehole to the sheds has a tap. Flow rate was measured at each tap by recording the time to fill a bucket. It is noted that flow rate tests on boreholes BH2 and BH3 during did not capture all the flow as some was going to the chickens. Results are shown in Table 5.2.

Table 5.2 Instantaneous flow rates (approximate)

| Borehole | Flow rate (l/s) |
| --- | --- |
| BH1 | 0.7 |
| BH2 | 0.7 |
| BH3 | 1.4 |
| Total | 2.84 |
| Total assuming half of flow at BH2 and BH3 to chickens | 5.0 |

Borehole parameters obtained during the test are shown in Table 5.3. Groundwater levels at BH1, BH2, and BH3 during the test period are shown in Figure 5.2.

Table 5.3 Borehole parameters

| Parameter | BH1 | BH2 | BH3 | Total |
| --- | --- | --- | --- | --- |
| Ground level (m aOD)1 | 245 | 244 | 242 |  |
| Pump depth (m bgl) | 64 | 68 | 61 |  |
| Rest water level (m bgl)2 | 6 | 8 | 6 |  |
| Maximum pumped water level (m bgl) | 49 | 68 | 23 |  |
| Average pumped water level (m bgl) | 10.2 | 24.6 | 14.7 |  |
| Average drawdown (m) | 4.2 | 16.6 | 8.7 |  |
| Average daily flow during growing cycle (m3/day) | 9 | 17 | 17 | 43 |
| Average annual flow (m3/year)3 | 2,500 | 4,800 | 4,800 | 12,100 |

1Approximate: obtained using Google Earth

2Inferred

3Assuming 37 days growing and 11 days rest (with no abstraction during rest days)

Figure 5.2 Groundwater level during test period

The following points are noted:

- Rest water level was not observed during the test therefore was inferred by extrapolating the recovery curves.

- During the growing cycle the boreholes did not run dry. However, the borehole pumps stay on for a short duration (a matter of minutes), therefore the logging frequency of 5 minutes could be insufficient to capture the full extent of the drawdown for each occasion the pump is on.

- During the washdown period (19 – 21 July) BH2 briefly ran dry on four occasions. Maximum drawdown was also seen in BH1 during this period. Water used during the washdown is not on a meter therefore the volumes and abstraction rates were not recorded. However, these are estimated in Table 5.4, by comparing the groundwater level drawdown in the growing cycle and in the washdown (see Appendix C).

Table 5.4 Estimated washdown rates and volumes

| Parameter | Unit | BH1 | BH2 | Total |
| --- | --- | --- | --- | --- |
| Washdown rate | l/s | 1.00 | 1.98 | 5.0 |
|  | m3/hr | 3.58 | 7.13 | 17.8 |
| Volume used during washdown | m3 | 10.75 | 110.44 | 121 |
|  | m3/d | 3.58 | 36.81 | 40 |

- Groundwater levels within the boreholes did not appear to be significantly influenced by pumping in the neighbouring boreholes. This is most clearly seen during the wash down and recovery period (20 July onwards)

Appendix C: Calculations

Table 1: Average daily flow measured during site investigations

| Unit | BH1 | BH2 | BH3 | Total | Comment |
| --- | --- | --- | --- | --- | --- |
| m3/d | 8.6 | 17.1 | 17.1 | 42.8 | Recorded |
| m3/hr | 0.4 | 0.7 | 0.7 | 1.8 | Pro-rata’d from daily |
| l/s | 0.1 | 0.2 | 0.2 | 0.5 | Pro-rata’d from daily |
| m3/a | 2420 | 4811 | 4811 | 12042 | Total during growing period (37 days growing and 11 days rest. Doesn't include washdown |

From graph in Figure 5.2, perhaps 5 x more drawdown is observed at BH2 whilst washdown pumping is on. To be conservative, assume linear correlation drawdown vs flow rate, and 10 x more drawdown.

Table 2: Hours pumping at full rate during washdown

| Date | Unit | BH1 | BH2 | BH3 |
| --- | --- | --- | --- | --- |
| 19/07/2023 | hrs | 0 | 5 | 0 |
| 20/07/2023 | hrs | 0 | 5.5 | 0 |
| 21/07/2023 | hrs | 3 | 5 | 0 |
| Total hrs pumping at max rate | hrs | 3 | 15.5 | 0 |

Table 3: Estimated washdown rates and volumes

|  | Unit | BH1 | BH2 | BH3 | Total |
| --- | --- | --- | --- | --- | --- |
| Washdown rate If 10 x hourly rate during growing cycle | l/s | 1.00 | 1.98 | 1.98 | 5.0 |
|  | m3/hr | 3.58 | 7.13 | 7.13 | 17.8 |
| Volume used during washdown | m3 | 10.75 | 110.44 | 0 | 121 |
|  | m3/d | 3.58 | 36.81 | 0 | 40 |

No. growing cycles per year: 7.6

Table 4: Annual volume used during washdown

|  | BH1 | BH2 | BH3 | Total |
| --- | --- | --- | --- | --- |
| m3 | 812 | 840 | 0 | 922 |

Table 5: Required abstraction quantities (detailed)

| Timescale |  | Value | Unit | How derived |
| --- | --- | --- | --- | --- |
| Annual | Growing | 13420 | m3/a | Max historic plus 10% increase for climate change |
|  | Washdown | 922 | m3/a | Not recorded. Conservative estimate from groundwater graph |
|  | Total | 14342 | m3/a |  |
|  |  | 39 | m3/d | equivalent |
| Daily | Growing | 83 | m3/d | Max historic plus 10% increase for climate change |
|  | Washdown | 40 | m3/d | Not recorded. Conservative estimate from groundwater graph |
| Hourly | Growing | 3 |  | Not recorded. Pro-rata'd from daily value |
|  | Washdown | 18 | m3/hr | Not recorded. Conservative estimate from groundwater graph, if all 3 BHs pumping at once (they are only on for a few hours per day) |
| Instantaneous | Growing | 5.0 | l/s | Not known. Estimated during site visit (from taps) |
|  | Washdown | 5.0 | l/s | Pro-rata'd from hourly value |

Items highlighted in cream to be carried through to summary table

Table 6: Required abstraction quantities (summary)

| Timescale | Value | Unit |
| --- | --- | --- |
| Annual | 14342 | m3/a |
| Daily | 83 | m3/d |
| Hourly | 18 | m3/hr |
| Instantaneous | 5.0 | l/s |

See Section 5.2 of report

Growing cycle ran from 12 June to 18 July