	CONSENT NO.
	BJ0091401


	CONSENT NO.
	BJ0091401

	SCHEDULE NO.
	BJ0091401 01



WATER RESOURCES ACT 1991

SECTION 88 – SCHEDULE 10

(AS AMENDED BY THE ENVIRONMENT ACT 1995)

NOTICE OF MODIFICATION OF CONSENT TO DISCHARGE

TO:
Environment Quality Scientist
Dŵr Cymru Cyfyngedig

         
Pentwyn Road

Nelson

Treharris

CF46 6LY
	Following a review of the conditions of its consent, the ENVIRONMENT AGENCY ("The Agency") in pursuance of its powers under the Water Resources Act 1991 HEREBY MODIFIES ITS CONSENT to the making of a discharge OF SEWAGE EFFLUENT, as follows:

Secondary Treated Sewage Effluent incorporating the requirements of the Urban Waste Water Treatment Regulations 1994 (UWWTR)

with respect to Modification of Consent No. BJ0091401 issued on the 31st day of October 2007

	FROM:
LLANYBYDDER WASTEWATER TREATMENT WORKS

	AT:
LLANYBYDDER, NEAR LAMPETER, CEREDIGION

	TO: 
RIVER TEIFI

	HEREAFTER SUBJECT TO the conditions set out in the following schedule(s):

Secondary Treated Sewage Effluent

      Schedule No. BJ0091401 01

UWWT Regulations 1994



      Schedule No. BJ0091401 01 / U

	Subject to the provisions of Paragraphs 7 and 8 of Schedule 10 of the Water Resources Act 1991, no notice shall be served by the Agency, which affects the effect of modifications made by this notice, without the agreement in writing of the Consent Holder, during a period of 4 years from the date this notice is served.

	Dated this 01st day of February 2008.


Signed    [image: image1.png]H A Bicher





 Team Leader – National Permitting Service


CONDITIONS OF CONSENT TO DISCHARGE

Secondary Treated Sewage Effluent (“the Discharge”)

FROM:
LLANYBYDDER WASTEWATER TREATMENT WORKS, LLANYBYDDER, NEAR LAMPETER, CEREDIGION

NATURE


1.
The Discharge shall consist solely of secondary treated sewage effluent.

LOCATION

2.
The Discharge shall be made in the manner and at the place specified as:

(a) discharging via a 150 millimetre diameter pipe;

(b) discharging to the River Teifi;

(c) at National Grid Reference SN 51724 43265;

(d) shown marked ‘Consent Point’ on Plan BJ0091401 attached as Annex 3.

SAMPLE POINT

3.
An appropriately labelled sample point shall be provided and maintained at National Grid Reference SN 51602 43144, as shown marked 'UWWTD FE Sampling Point' on Plan BJ0091401, or some other point as agreed in writing with the Agency, so that a representative spot sample of the Discharge may be obtained. The consent holder shall ensure that all constituents of the Discharge pass through the said sampling point at all times and in any legal proceedings it shall, for the purposes of Section 10 of the Rivers (Prevention of Pollution) Act 1961, be presumed, until the contrary is shown that any sample of the Discharge taken at the said sampling point is a sample of what was being discharged into controlled waters.

VOLUME

4. The volume of the Discharge shall not exceed 2,376 cubic metres per day.

5.
The Dry Weather Flow of the Discharge shall not exceed 1,019 cubic metres per day.

For the purpose of this condition Dry Weather Flow shall mean the average daily flow to the treatment works during seven consecutive days without rain (excluding a period which includes public holidays) following seven days during which the rainfall did not exceed 0.25 millimetres on any one day.

6.
The rate of discharge shall not exceed 27.5 litres per second.

FLOW MEASUREMENT
7. A continuous flow monitoring and recording system, to a specification provided by the Agency, with on-site visual display from which readings can be readily obtained by the Agency, shall be provided and operated to record the daily volume and instantaneous flow of the discharge.

8. As soon as practicable after completion of the flow system installation the Consent Holder shall employ an independent expert to certify that the installation complies with the Agency’s specification. The Consent Holder shall satisfy himself as to the professional competence of the expert. A copy of the certifier’s report shall be provided to the Agency when it is available.

9.
Records of the flow readings shall be maintained by the Consent Holder and shall be provided to the Agency when requested, in a format specified by the Agency.

10. The Consent Holder shall produce and maintain a quality control manual, approved by the independent expert and to the satisfaction of the Agency, specifying procedures for the calibration, operation and maintenance of the flow monitoring system. The flow system shall be calibrated, operated and maintained by the Consent Holder in accordance with the provisions of the manual. The Consent Holder shall keep a record of these procedures available for inspection by the Agency and provide a copy to the Agency on request.

11. The Consent Holder shall record all failures of the continuous flow system and any other breaks in the flow record. The reasons for these failures and breaks shall be recorded and all steps taken to prevent a re-occurrence. The Consent Holder shall ensure that as far as possible the recorder remains fully operational at all times. Any failures shall be remedied as soon as possible.
12. Flows passing forward to full treatment shall be measured at Llanybydder Terminal Sewage Pumping Station at National Grid Reference SN 51938 43403, or such other point(s) as agreed by the Agency.

COMPOSITION

13. (a)
Subject to paragraph (c) below, the Discharge shall not contain more than:

(i) 40 milligrammes per litre of biochemical oxygen demand (measured after 5 days at 20oC with nitrification suppressed by the addition of allyl‑thiourea);

(ii) 60 milligrammes per litre of suspended solids (measured after drying at 105oC).

 (b)
During the periods specified, and subject to paragraph (c) below, the Discharge shall not contain more than:

(i) 60 milligrammes per litre of ammoniacal nitrogen (expressed as N) until 31st August 2008;

(ii) 5 milligrammes per litre of ammoniacal nitrogen (expressed as N) henceforth from 1st September 2008.

(c)
The limit for any of the relevant parameters set out in paragraphs (a) and (b) above may be exceeded where, in any series of samples of the Discharge taken at regular but randomised intervals in any period of twelve consecutive months as listed in Column 1 of the table at Annex 1 to this consent, no more than the relevant number of samples, as listed in Column 2 of the said table, exceed the applicable limit for that relevant parameter.
14. (a)
The Discharge shall not contain more than 80 milligrammes per litre of biochemical oxygen demand (measured after 5 days at 20oC with nitrification suppressed by the addition of allyl‑thiourea);

(b) During the periods specified, the Discharge shall not contain more than:

(i) 120 milligrammes per litre of ammoniacal nitrogen (expressed as N) until 31st August 2008;

(ii) 20 milligrammes per litre of ammoniacal nitrogen (expressed as N) henceforth from 1st September 2008.

WORKS OPERATION

15.
The works shall be operated and the effluent shall be treated in a manner which, so far as reasonable practicable, minimises the polluting effects of the discharge made from the works on controlled waters.

This condition does not require -


(a)
any higher standard to be achieved in relation to any characteristic of the discharge which is specifically regulated by conditions 13 and 14, than is required by those conditions;


(b)
any alteration of the works or a change in the type of treatment used.

UNUSUAL WEATHER CONDITIONS
16. 
(a)
No sample of the discharge, taken at a time when unusual weather conditions are adversely affecting the operation of the sewage treatment works, shall be taken into account in deciding whether or not the conditions 13, 14 and 15 of this consent have been complied with.

(b)
For the purpose of this condition "unusual weather conditions" shall include:

(i)
low ambient temperatures as evidenced by effluent temperatures of 5oC or less, or by the freezing of mechanical equipment in the works;


(ii)
significant snow deposits;


(iii)
tidal or fluvial flooding;


(iv)
weather conditions causing unforeseen loss of power supply to the sewage treatment which could not be ameliorated by the reasonable provision and operation of standby generation facilities.

(c) On any occasion where unusual weather conditions adversely affect the operation of the sewage treatment works, the Consent Holder shall use its best endeavours to mitigate that adverse effect.


(d)
For a sample of the discharge to be considered for the purposes of (a) above, the Consent Holder shall notify the Agency by telefax or telephone as soon as unusual weather conditions are known to have adversely affected operations and shall confirm the circumstances in writing as soon as possible thereafter (and in any event within 14 days of the occurrence of such conditions). That notification shall include a full description of the unusual weather conditions and their impact on the operation of the works.

RECORDING AND REPORTING
17.
(a)
The Consent Holder shall establish and operate a documented maintenance programme and record all non-routine actions undertaken that may have adversely affected effluent quality. Copies of the programme shall be made available for inspection by the Agency's officers at all reasonable times.

(b) On request the Consent Holder shall supply the Agency with a written report on the maintenance and all non-routine actions that may have adversely affected effluent quality.

18.
The Consent Holder shall notify the Agency in writing if any known or planned introduction or material change in respect of discharges from trade premises to the sewerage system occurs, that may increase or introduce into the effluent any "dangerous substance" included on Lists I, II, or Red List (set out in Annex 2 to this notice as updated from time to time and notified to the Consent Holder in writing), and any other substance considered by the Consent Holder as having or likely to have a significant effect on the receiving waters.

SUBSTANTIAL CHANGE
19.
A discharge shall not be made from the works if it would cause a significant increase in the polluting effects of the discharge on controlled waters as a result of a new or altered discharge of trade effluent into the works.

19.1
A discharge of trade effluent into the works is new if -

(a) it is made by the sewerage undertaker and is of a kind not made into the works by the undertaker immediately before the date of effect of this consent; or

(b) it is made by a third party and the discharge is authorised on or after that date.

19.2
A discharge of trade effluent into the works is altered if -

(a) it is made by the sewerage undertaker and its composition or quantity changes significantly on or after the date of effect of this consent; or

(b) it is made by a third party and the alteration of the discharge is authorised on or after that date.

19.3
An increase in the polluting effects of the Discharge on controlled waters is not significant for the purposes of this condition if it relates to any characteristic of the Discharge which is specifically regulated by conditions 13 and 14 of this consent but it may be significant if it is caused by a change in some other characteristic of the Discharge.

19.4
For the purposes of this condition “trade effluent” means -

(a)
any discharge by the sewerage undertaker other than

(i) 
domestic sewage from premises connected directly or indirectly to the works; or

(iii) surface water run-off;

(b) any discharge by a third party which is authorised under Chapter III of Part IV of the Water Industry Act 1991 or which is only accepted as a result of a contract with the sewerage undertaker.

UNAUTHORISED DISCHARGES
20.
A discharge made from the works shall not contain any poisonous, noxious or polluting matter or solid waste matter which is attributable to any unauthorised discharge into the works.

(a)
A discharge into the works is unauthorised if it is made by a third party and either there is no obligation to receive it or conditions subject to which there is an obligation to receive it are not observed.

(b) Nothing in this, or any other, condition of this consent prevents anyone from relying on any defence available to them under section 87 of the Water Resources Act 1991.

CONDITIONS OF CONSENT TO DISCHARGE

ADVANCE \u12 Secondary Treated Sewage Effluent ("the Discharge")

FROM:
LLANYBYDDER WASTEWATER TREATMENT WORKS, LLANYBYDDER, NEAR LAMPETER, CEREDIGION

URBAN WASTE WATER TREATMENT REGULATIONS
U0
(a)
The Consent Holder shall comply with the Urban Waste Water Treatment (England and Wales) Regulations 1994 ('the Regulations').

(b)
For the purpose of conditions U1 and U2 below, interpretations and references to a numbered regulation or Schedule shall have the meaning as in the Regulations, unless otherwise indicated.
U1
(a)
The Discharge derives from an agglomeration with a population equivalent of between 2,000, and 10,000, discharging to freshwaters.
(b)
The Consent Holder shall inform the Agency in writing of any change, or proposed change, to the population equivalent such as would make a material change to the application of the Regulations and shall, on request, inform the Agency in writing of the actual population equivalent. 

(c)
The Discharge shall be subject to Regulation 5(1) and shall satisfy the requirements of Part I of Schedule 3.

U2
(a)
The Consent Holder shall provide apparatus for the purpose of:

(i) measuring or recording the volume, rate of flow, nature, composition or temperature, and


(ii) collecting samples of any waste water,

as is necessary to ensure compliance with paragraph (b) below.

(b)
The Consent Holder shall monitor the Discharge to verify compliance with the requirements of condition U1(c) above in accordance with control procedures as set out in Part II of Schedule 3.
(c)
The Consent Holder shall provide to the agency any information collected in complying with paragraph (b) above in a manner agreed with the agency.

U3
Condition U2 above shall apply for the purpose of verifying compliance with the directive from the date as specified in the relevant paragraph of regulation 5 as incorporated into this consent under condition U1(c) above.

U4
(a)
An appropriately labelled sample point shall be provided and maintained at National Grid Reference SN 51937 43408, as shown marked ‘UWWTD Crude Sampling Point’ on the attached Plan No. BJ0091401, or some other point as agreed in writing with the Agency, so that a representative sample of the Influent may be obtained.

(b)
an appropriately labelled sample point shall be provided and maintained at National Grid Reference SN 51602 43144, as shown marked ‘UWWTD FE Sampling Point’ on the attached Plan No. BJ0091401, or some other point as agreed in writing with the agency, so that a representative sample of the discharge may be obtained.

ANNEX 1
TABLE

              
       Column 1                        
   
     
Column 2
ADVANCE \u12
           
Number of samples                     

Maximum number of samples

          

taken in any period                        
   permitted to exceed limit

             
    of 12 months                               
     for given determinand

                 

  4‑7                                       


1

                 

  8‑16                                      


2

                

17‑28                                      


3

                

29‑40                                      
 

4

                

41‑53                                      
 

5

                

54‑67                                      


6

                

68‑81                                      
  

7

                

82‑95                                      
  

8

                

96‑110                                     
  

9

               
          111‑125                                    


10

               
          126‑140                                    


11

               
          141‑155                                    


12

               
          156‑171                                    


13

               
          172‑187                                    


14

               
          188‑203                                    


15

               
          204‑219                                    


16

               
          220‑235                                    


17

               
          236‑251                                    


18

               
          252‑268                                    


19

               
          269‑284                                    


20

               
          285‑300                                    


21

               
          301‑317                                    


22

               
          318‑334                                    


23

               
          335‑350                                    


24

               
          351‑365                                    


25

ANNEX 2

 1.
Mercury and its compounds

2.
Cadmium and its compounds

 3.
Hexachlorocyclohexane


4.
Carbon tetrachloride


(lindane and related compounds)

 5.
DDT (the isomers of 1,1,1‑trichloro‑2,2  bis{p‑chlorophenyl} ethane)

 6.
Pentachlorophenol (PCP)


7.
Aldrin

 8.
Dieldrin




9.
Endrin

10.
Isodrin 




11.
Hexachlorobenzene (HCB)

12.
Hexachlorobutadiene (HCBD)

13.
Chloroform

14.
Polychlorinated biphenyls


15.
Dichlorvos

16.
1,2‑Dichloroethane


17.
Trichlorobenzene

18.
Atrazine




19.
Simazine

20.
Tributyltin compounds


21.
Triphenyltin compounds

22.
Trifluralin



23.
Fenitrothion

24.
Azinphos‑methyl



25.
Malathion

26.
Endosulfan



27.
Lead

28.
Chromium



29.
Zinc

30.
Copper




31.
Nickel

32.
Arsenic




33.
*Iron

34.
*pH outside range 5.5 to 9.0

35.
*Boron

36.
Vanadium



37.
PCSD'S

38.
Cyfluthrin



39.
Sulcofuron

40.
Flucofuron



41.
Permethrin

42.
4-Chloro-3-methyl-phenol


43.
2-Chlorophenol

44.
2,4-Dichlorophenol


45.
2,4-D (ester)

46.
2,4-D (non ester)



47.
1,1,1-Trichloroethane

48.
1,1,2-Trichloroethane


49.
Bentazone

50.
Benzene



51.
Biphenyl

52.
Chloronitrotoluenes


53.
Demeton

54.
Dimethoate



55.
Linuron

56.
MCPA 




57.
Mecoprop

58.
Mevinphos



59.
Napthalene

60.
Omethoate



61.
Toluene

62.
Triazophos



63.
Xylene


64.
Cyanide




65.
Azinphos‑ethyl

66.
Fenthion



67.
Parathion

68.
Parathion‑methyl



69.
Trichloroethylene

70.
Tetrachloroethylene


71.
Dioxins

72.
PAHs 




73.
Nonyl phenol 

74.
Nonyl phenyl ethoxylate 


75.
Di-ethylhexyl phthalate 

76.
Bisphenol-A 



77.
Diazinon 

78.
Chlorfenvinphos 



79.
Chlorotoluron 

80.
Isoproturon



81.
Diuron

82.
Propetamphos 



83.
Flumethrin 

84.
Amitraz 




85.
High-Cis Cypermethrin 

86.
Cyromazine 



87.
Deltamethrin

88.
Cypermethrin  

This list is applicable as at 1 December 1998 and will be updated as and when changes to the relevant legislative requirements occur.

*Notification to the Agency by the Consent holder is only required in respect of changes to trade effluents likely to cause significant changes to the pH value, and/or iron or boron concentrations, of the crude sewage.

Page 2 of 12

