## READ ME
Special Area of Conservation Permit Review - Water Discharge Activities (DCWW) - Regulation 61 Notice Response Tool
This Excel file has been put together to enable DCWW to provide a structured response to the Regulation 61 Notice for the Special Area of Conservation Permit Review.
All of the information in the 'Reg61 Response Sheet' must be completed for each asset to enable NRW to complete the Regulator Initiated Variations, use the information below to complete the sheet:
Explanation & Key Information (Reg61 Response Sheet):
  Colour Key (Row 2):
- Headings in Blue contain identification information (e.g. Permit number) or miscellaneous information that shows where further information is required (e.g. other relevant NEP Drivers to be included in variation)
- Headings in Green contain information on the permit (e.g. Permitted DWF, weir setting)
- Headings in Yellow contain information required to be provided to complete the review or allow the permit to be drafted (e.g. new P limit, site plan)
  Discharge Type:
- Columns A-V are relevant to the Final Effluent permit
- Columns W-AE are relevant to the Storm permit
- Columns AF-AJ are relevant to the Emergency permit
- Storm and Emergency information should only be complete if the permits are to be consolidated into the Final Effluent permit, if there is not a Storm/Emergency discharge at the site or if DCWW do not want a permit consolidation the boxes should contain 'N/A'
  Other:
- If there is a consolidation, new Site Plans (Column Q) and Bespoke Conditions (Column R) should consider this and include the relevant information
- If another document is required (NEP Driver Permit information/New Site Plan), it should be named in the sheet as per the document. The submission format, timing and procedure for supplyingthis information should be agreed with NRW Permitting Service

## Reg61 Response Sheet
Final Effluent Permit | [21 empty] | Storm Permit | [9 empty] | Settled Storm | [9 empty] | UV Treatment |  |  |  |  | Emergency Permit
Site Name | Permit Number | Any other permits to be consolidated into the FE permit? ▪Storm = columns V - AF ▪Settled Storm = columns AG - AP ▪UV Pre and Post Treatment = columns AQ - AU ▪Emergency = columns AV - AZ | Other NEP Driver to be included in variation? | Permitted DWF (m³/d) | FE Permit in EPR Format? | Site address | Receiving Watercourse | FE dicharge point NGR | FE sample point | UWWTD inlet sample point | UWWTD outlet sample point | MCERTS flow meter | Current Permit Limits | Bespoke Conditions Required? ▪Limits of Specified Activity ▪Operating Techniques ▪Pre-Op/Improvement Conditions | New Site Plan Required? | Site Plan File Name (.jpg or .pdf) - to include any consolidated permits | Bespoke Condition File Name (.doc) - to include any consolidated permits | Proposed Total Phosphorus as P Limit | Proposed P limit Sampling Method | Proposed Total Aluminium as Al Limit | Information for Other NEP Variations? (.doc, .xlsx) | Permit Number2 | Storm Permit in EPR Format? | Storm sewage discharge point | Storm sewage effluent sample point | Storm sewage discharge EDM (AMP6) NGR | Overflow setting (l/s) or weir height (if reverse flow/both) (Table S3.3) | Storm storage volume (m³) (Table S3.3) | Online or Offline storage? (Table S3.3) | Maximum size of solid matter (Table S3.3) | Screen aperture size (mm) (Table S3.3) | Permit Number3 | Settled Storm Permit in EPR Format? | Settled Storm sewage discharge point | Settled Storm sewage effluent sample point | Settled Storm sewage discharge EDM (AMP6) NGR | Overflow setting (l/s) or weir height (if reverse flow/both) (Table S3.3)4 | Settled Storm storage volume (m³) (Table S3.3) | Online or Offline storage? (Table S3.3)5 | Maximum size of solid matter (Table S3.3)6 | Screen aperture size (mm) (Table S3.3)7 | Permit Number8 | UV Treatment Permit in EPR format | UV effluent discharge point | UV pre-treatment effluent sample point | UV post-treatment effluent sample point | Permit Number9 | Emergency Permit in EPR Format? | Sewage in emergency discharge point NGR | Sewage in emergency effluent sample point NGR | PKPSM File Name (.doc)
CEFN GORWYDD - refer to column S | AN0180001 | [16 empty] | No requirement. NRW believe DWF > 20 m3/d, and therefore a backstop is needed. Please supply evidence if this is the case.
CELLAN | BN0008101 | No | No | 34.1m³/d | Yes | Cellan Wastewater Treatment Works, Tre Cynon Street, Lampeter, Ceredigion, SA48 8HZ. | Drain to Afon Teifi | SN 60129 49105 | SN 60253 49052 | N/A | N/A | SN 60256 49035 | N/A - Descriptive. | N/A | No | N/A | N/A | 5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 30/09/2023). | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CENARTH CEREDIGION | BP0101201 | Yes - Settled Storm in Emergency (BP0101202) & Storm (BP0101203) | Yes - UMon3/4 | 152m³/d | No | Cenarth Wastewater Treatment Works, Glanyrafon, Cenarth, Ceredigion, SA38 9JR | Afon Teifi | SN 26579 41662 | SN 26557 41681 | N/A | N/A | SN 26544 41704 | LuT (95%ile) Limits: 40mg/l BOD & 60mg/l SS. | N/A | Yes | Permits_drawing1__BP0101201 | N/A | 5mg/l - start date 2030. *Insufficient samples to accept backstop immediately (samples collected by 30/09/2023). | Spot | N/A | U_MON3 4 Permitting Information | BP0101203 | Yes | SN 26579 41662 | SN 26555 41701 | SN 26531 41706 | 9.46l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | BP0101202 | No | SN 26570 41660 | SN 26557 41681 | Not available currently with OPS
CERRIGYDRUDION | CM0052101 | Yes - Storm (CG0438301) | Yes - UMon3/4 | 111m³/d | Yes | Cerrigyrdrudion Wastewater Treatment Works, Off A5, Cerrigidrudion, Corwen, LL21 9SY | Afon Nug | SH 95258 48277 | SH 95269 48326 | N/A | N/A | SH 95270 48328 | LuT (95%ile) Limits: 40mg/l BOD, 10.5mg/l NH3 & 60mg/l SS. | N/A | Yes | Permits_drawing1__CM0052101 | N/A | 1mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/05/2024). | 24hr Composite | N/A | U_MON3 4 Permitting Information | CG0438301 | Yes | SH 95258 48277 | SH 95271 48336 | SH 95277 48369 | 7l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CILCAIN PANTYMWYN | CM0024401 | No | No | 241m³/d | No | Cilcain/ Pantymwyn Sewage Treatment Works, Hesp Alyn Farm, Cilcain, Mold, CH7 5NL | Afon Alyn | SJ 19104 65505 | SJ 19119 65566 | N/A | N/A | SJ 19163 65561 | LuT (95%ile) Limits: 100mg/l BOD & 75mg/l SS. pH 5-9 maximum range. | N/A | Yes | CM0024401 Site Plan | N/A | 5mg/l - start date 2030. *Current samples show P concentration cannot meet backstop, investment is required. Cannot accept backstop immediately. | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CLARBESTON | BG0014501 | Yes - Storm (BG0014502) | Yes - UMon3/4 | 84m³/d | Yes | Clarbeston Wastewater Treatment Works, Clarbeston Road, Pembrokeshire, SA63 4UN. | Cartlett Brook | SN 01096 20967 | SN 01124 20973 | N/A | N/A | SN 01137 20962 | LuT (95%ile) Limits: 20mg/l BOD, 8mg/l NH3 & 30mg/l SS. | N/A | Yes | Permits_drawing1__BG0014501 | N/A | 1.5mg/l - start date 2030. | 24hr Composite | N/A | U_MON3 4 Permitting Information | BG0014502 | Yes | SN 01130 20982 | SN 01142 20973 | SN 01139 20960 | 7.4l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
COEDWAUNGAER - refer to column S | AB0043501 | [16 empty] | No requirement. NRW believe DWF > 20 m3/d, and therefore a backstop is needed. Please supply evidence if this is the case.
CRADOC PHASE 1 - refer to column S | AN0035901 | [16 empty] | No requirement. NRW believe DWF > 20 m3/d, and therefore a backstop is needed. Please supply evidence if this is the case.
CRIBYN | BG0027001 | Yes - Storm (BG0027002) | No | 34.1m³/d | Yes | Cribyn Wastewater Treatment Works, Cribyn, Lampeter, Ceredigion, SA48 7HQ | Afon Grannell | SN 51542 51158 | SN 51561 51193 | N/A | N/A | SN 51561 51193 | LuT (95%ile) Limits: 40mg/l BOD & 45mg/l SS. | N/A | No | N/A | N/A | 3.5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/05/2024). | Spot | N/A | N/A | BG0027002 | Yes | SN 51548 51161 | SN 51576 51181 | SN 51576 51181 | 4.5l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CROESOR - NEW WORKS | CG0133001 | No | No | 24.3m³/d | No | Croesor WwTW, Penrhyndeudraeth, Croesor, LL48 6SR | Afon Croesor | SH 62997 44592 | SH 63004 44586 | N/A | N/A | N/A | LuT (95%ile) Limits: 150mg/l BOD & 150mg/l SS. | N/A | Yes | CG0133001 Site Plan | N/A | 5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/12/2023). | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CWRT HENRI CARMS | BN0018001 | Yes - Storm (BP0316701) | No | 40.4m³/d | No | Cwrt Henri Wastewater Treatment Works, Nr Maes Awelon, Carmarthen, Carmarthenshire, SA32 8SA | Afon Dulas | SN 55653 22694 | SN 55416 22821 | N/A | N/A | N/A | LuT (95%ile) Limits: 20mg/l BOD, 30mg/l SS & 10mg/l NH3. | N/A | Yes | BN0018001 Site Plan | N/A | 5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/12/2023). | Spot | N/A | N/A | BP0316701 | Yes | SN 55653 22694 | SN 55406 22823 | SN 55406 22823 | 3l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
DINGESTOW MONMOUTH | AS1000701 | No | No | Unclear at this stage - under query due to PE. | No | Dingestow Wastewater Treatment Works, Dingestow, Monmouth, Gwent, NP25 4BY | River Trothy | SO 45926 10066 | SO 45800 10046 | N/A | N/A | N/A | N/A - Descriptive. | N/A | Yes | AS1000701 Site Plan | N/A | 5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/12/2023). | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
DINMAEL - refer to column S | CM0038801 | [16 empty] | No requirement. NRW believe DWF > 20 m3/d, and therefore a backstop is needed. Please supply evidence if this is the case.
DOLYWERN | CM0007901 | Yes - Storm (CM0009501) | Yes - UMon3/4 | 50m³/d | No | Dolywern Wastewater Treatment Works, Old road, Dol-Y-Wern, Wrexham, LL20 7AY | River Ceiliog | SJ 22440 37250 | SJ 22439 37226 | N/A | N/A | SJ 22429 37205 | LuT (95%ile) Limits: 150mg/l BOD, 150mg/l SS & 50mg/l NH3. | N/A | Yes | Permits_drawing1__CM0007901 | N/A | 2mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/10/2023). | 24hr Composite | N/A | U_MON3 4 Permitting Information | CM0009501 | Yes | SJ 22408 37215 | SJ 22429 37209 | SJ 22429 37209 | 1.62l/s | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
ELAN VILLAGE - refer to column S | AW1001401 | [16 empty] | No requirement. NRW believe DWF > 20 m3/d, and therefore a backstop is needed. Please supply evidence if this is the case.
FELINGWM | BJ0075601 | Yes - Storm (BP0328301) | No | 22m³/d | No | Felingwm Wastewater Treatment Works, Nr Blaenparc House, Felingwm, Carmarthen, SA32 7PR | Cloidach | SN 50867 24401 | SN 50874 24407 | N/A | N/A | N/A | LuT (95%ile) Limits: 40mg/l BOD, 51mg/l SS & 10mg/l NH3. | N/A | Yes | BJ0075601 Site Plan | N/A | 5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/12/2023). | Spot | N/A | N/A | BP0328301 | Yes | SN 50867 24401 | SN 50874 24407 | SN 50874 24407 | 1.2l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
FFOSTRASOL | BH0072801 | No | No | 31.8m³/d | No | Ffostrasol Wastewater Treatment Works, Ffostrasol, Llandysul, Ceredigion, SA44 4TA | Afon Cerdin Fach | SN 37793 47554 | SN 37444 47381 | N/A | N/A | N/A | LuT (95%ile) Limits: 20mg/l BOD & 42mg/l SS. | N/A | Yes | BH0072801 Site Plan | N/A | 4.5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/05/2024). | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
FRONGOCH | CM0077301 | No | No | Unclear at this stage - under query due to PE. | No | Frongoch Wastewater Treatment Works, Frongoch, Y Bala, Gwynedd, LL23 7NT | Afon Tryweryn | SH 90559 39124 | SH 90559 39156 | N/A | N/A | N/A | N/A - Descriptive. | N/A | Yes | CM0077301 Site Plan | N/A | 5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/10/2023). | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GARTH | AW1002001 | No | No | 27.3m³/d | No | Garth Wastewater Treatment Works, Garth, Llangammarch Wells, LD4 4AF | Dulas Brook | SN 95097 49218 | SN 95129 49244 | N/A | N/A | N/A | N/A - Descriptive. | N/A | Yes | AW1002001 Site Plan | N/A | 5mg/l - start date 2030. *Insufficient samples to accept backstop immediately (samples collected by 30/09/2023). | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GORSGOCH - refer to column E | BG0043501 |  |  | Not a site we consider for RoP as the DWF is below 20m³/d. | [13 empty] | 3mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 31/05/2024).
GROESFFORDD | AD0018101 | No | No | 36m³/d | No | Groesffordd Wastewater Treatment Works, Groesfford, Brecon, Powys, LD3 7SN | Brynich Brook | SO 07371 27873 | SO 07397 27883 | N/A | N/A | N/A | N/A - Descriptive. | N/A | Yes | AD0018101 Site Plan | N/A | 5mg/l - start date 2030. | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GROSMONT | AH1001001 | No | No | 38m³/d | Yes | Grosmont Wastewater Treatment Works, Grosmont, Abergavenny, Monmouthshire, NP7 8LW | River Monnow | SO 40901 24260 | SO 40901 24260 | N/A | N/A | SO 40907 24219 | N/A - Descriptive. | N/A | No | N/A | N/A | 5mg/l - start date 2030. | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
GWENDDWR - refer to column S | AW1002201 | [16 empty] | No requirement. NRW believe DWF > 20 m3/d, and therefore a backstop is needed. Please supply evidence if this is the case.
GWYNFE CAPEL GWYNFE - refer to column S | BP0164501 | [16 empty] | No requirement. NRW believe DWF > 20 m3/d, and therefore a backstop is needed. Please supply evidence if this is the case.
HALTON | CM0022001 | No | No | 50m³/d | Yes | Halton Wastewater Treatment Works, Black Park, Halton, Wrexham, LL14 5BD | River Dee | SJ 30582 40592 | SJ 30416 40545 | N/A | N/A | SJ 30416 40545 | LuT (95%ile) Limits: 150mg/l BOD, 150mg/l SS & 50mg/l NH3. | N/A | No | N/A | N/A | 5mg/l - start date 2030. | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
KEESTON | BP0087901 | Yes Storm (BP0087902) | Yes - UMon3/4 | 129.2m³/d | Yes | Keeston Wastewater Treatment Works, Bridge Lane, Pembrokeshire, SA62 6EE | Knock Brook | SM 90815 18678 | SM 90809 18699 | N/A | N/A | SM 90786 18726 | LuT (95%ile) Limits: 20mg/l BOD, 30mg/l SS & 3mg/l NH3. | N/A | Yes | Permits_drawing_1_BP0087901 | N/A | 1.5mg/l - start date 2030. | 24hr Composite | N/A | U_MON3 4 Permitting Information | BP0087902 | Yes | SM 90801 18724 | SM 90789 18723 | SM 90788 18726 | 5.89 | N/A | N/A | No greater than 20 mm in more than 2 dimension | 20mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANARMON | CM0022101 | No | No | 17m³/d | No | Llanarmon Dyffryn Ceiriog Wastewater Treatment Works, Centenary Hall, Llanarmon, Dyffryn Ceiriog, LL20 7LD | Afon Ceiriog | SJ 15969 32875 | SJ 15980 32834 | N/A | N/A | N/A | N/A - Descriptive. | N/A | Yes | CM0022101 Site Plan | N/A | 1.5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 30/09/2023). | 24hr Composite | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
LLANARMON-YN-IAL | CM0001201 | Yes - Storm (CM0001202) & Emergency (CG0432501) | Yes - UMon3/4 application not yet submitted. | 64.5m³/d | No | Llanarmon-yn-Ial Wastewater Treatment Works, Llanarmon-yn-Ial, Mold, Denbighshire, CH7 4QY | River Alyn | SJ 19019 55938 | SJ 19009 55936 | N/A | N/A | SJ 19010 55941 | LuT (95%ile) Limits: 40mg/l BOD, 60mg/l SS & 15mg/l NH3. | N/A | Yes | CM0001201 Site Plan | N/A | 5mg/l - start date 2030. *Insufficient samples to accept backstop immediately (samples collected by 30/11/2023). | Spot | N/A | N/A | CM0001202 | Yes | SJ 19019 55938 | SJ 19009 55936 | SJ 19007 55938 | 3.4l/s | N/A | N/A | No greater than 6 mm in more than 1 dimension | 6mm x 6mm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | CG0432501 | No | SJ 19019 55938 | SJ 18996 55919 | CG0432501 PSKPM
LLANARTH MONMOUTHSHIRE | AC0091901 | No | No | 50m³/d | No | Llanarth Wastewater Treatment Works, Llanarth, Gwent, NP15 2AS | A tributary of the Clawdd Brook | SO 37783 10477 | SO 37682 10728 | N/A | N/A | SO 37681 10732 | LuT (95%ile) Limits: 30mg/l BOD, 45mg/l SS & 7mg/l NH3. 64mg/l BOD & 27mg/l NH3. | N/A | Yes | AC0091901 Site Plan | N/A | 5mg/l - start date 2032. *Insufficient samples to accept backstop immediately (samples collected by 30/09/2023). | Spot | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A