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Notice of variation and consolidation with introductory note
The Environmental Permitting (England & Wales) Regulations 2016
Dŵr Cymru Cyfyngedig
Rhydlafar Wastewater Treatment Works
Llantrisant Road
St Fagans
CARDIFF
CF5 6DS
Variation application number

PAN-005941
Permit number
AE2021601
Rhydlafar Wastewater Treatment Works
Permit number AE2021601
Introductory note

This introductory note does not form a part of the notice.
The following notice gives notice of the variation and consolidation of an environmental permit.
This is an ND1 (No Deterioration for ammonia) on the NEP for delivery this AMP year. It comprises a tightening of the current limits from 10mg/l BOD, 15 mg/l Suspended Solids and 5.5 mg/l Ammonia to 14 mg/l Suspended Solids, 9.5 mg/l BOD and 3 mg/l Ammonia. Due to growth in the catchment the DWF needs to be increased from 769m3/day to 792 m3/day. In addition, the current CSO will be permitted for flows above 6 X DWF: (36.3 l/s).
The schedules specify the changes made to the permit.
The status log of a permit sets out the permitting history, including any changes to the permit reference number.  It is not backdated before 6 April 2010. 
	Status log of the permit

	Description
	Date
	Comments

	Application

PAN-005941
(variation and consolidation)
	Duly made 14/08/2019
	Application to tighten the permit limits to 14 mg/l Suspended Solids, 9.5 mg/l BOD and 3 mg/l Ammonia. Also to increase the DWF from 769 to 792 m3/day and permit the current existing CSO.

	Additional information received
	28/02/2020
	Additional info re: spill analysis, calculation of DWF and EDM received.

	Variation determined PAN-005941 
	20/04/2020
	Varied and consolidated permit issued in modern condition format.


End of introductory note
	Notice of variation and consolidation 


The Environmental Permitting (England and Wales) Regulations 2016
The Natural Resources Body for Wales (“Natural Resources Wales”) in exercise of its powers under regulation 20 of the Environmental Permitting (England and Wales) Regulations 2016 varies and consolidates
Permit number

AE2021601
issued to:

Dŵr Cymru Cyfyngedig (“the operator”)

whose registered office is
Dŵr Cymru Cyfyngedig
Pentwyn Road
Nelson
Treharris
Mid Glamorgan

CF46 6LY
company registration number 02366777
to operate a regulated facility at
Rhydlafar Wastewater Treatment Works

Llantrisant Road

St Fagans

CARDIFF

CF5 6DS

to the extent set out in the schedules.
The notice shall take effect from 20/04/2020
	Name
	Date

	Amy Nethercott


	20/04/2020


Authorised on behalf of Natural Resources Wales
Schedule 1 

The following conditions were varied as a result of the application made by the operator:

· Conditions: 2.1, 2.2, 2.3, 3.1, 3.3 and 4.2
· Tables S1.1, S3.1, S3.2, S4.1 and S4.2 
· Schedules 3B, 4 and 7
The following conditions were varied as a result of an Natural Resources Wales initiated variation:

· Conditions: 1, 3.2 and 4.1

· Tables: S 3.3 and S 3.4

· Schedules 3A, 3C, 5 and 6

Schedule 2 – consolidated permit

Consolidated permit issued as a separate document. 

	Permit


The Environmental Permitting (England and Wales) Regulations 2016
Permit number 

AE2021601
This is the consolidated permit referred to in the variation and consolidation notice for application PAN-005941 authorising, 
Dŵr Cymru Cyfyngedig (“the operator”),

whose registered office is

Pentwyn Road
Nelson

Treharris

Mid Glamorgan

CF46 6LY

company registration number 02366777
to operate a water discharge activity at
Rhydlafar Wastewater Treatment Works

Llantrisant Road

St Fagans

CARDIFF

CF5 6DS

to the extent authorised by and subject to the conditions of this permit.

	Name
	Date

	  Amy Nethercott
	20/04/2020


Authorised on behalf of Natural Resources Wales

Conditions
1.1.1 Management

1.1 General management

1.1.1 The operator shall manage and operate the activities:
1.1.1 in accordance with a written management system that identifies and minimises risks of pollution so far as is reasonably practicable, including those risks arising from operations, maintenance, accidents, incidents, non-conformances and those drawn to the attention of the operator as a result of complaints; and

1.1.1 using sufficient competent persons and resources.

1.1.2 Records demonstrating compliance with condition 1.1.1 shall be maintained. 

1.1.3 Any person having duties that are or may be affected by the matters set out in this permit shall have convenient access to a copy of the permit.

2.1.1 Operations

2.1.1 Permitted activities

2.1.1 The only activities authorised by the permit are the activities specified in schedule 1 table S1.1.

2.2.1 The site 

2.2.1 The discharge activities shall take place at the discharge point marked on the site plan at schedule 7 to this permit, and as listed in table S3.2.

2.3.1 Operating techniques

2.3.1 For the activity A1 referenced in schedule 1, table S1.1 The operator shall comply with the relevant requirements of the Urban Waste Water Treatment (England and Wales) Regulations 1994.

2.3.2 
For the discharge(s) specified in table S3.3:

2.3.1 The discharge shall only occur when and only for as long as the flow passed forward is equal to or greater than the overflow setting indicated due to rainfall and/or snow melt.
2.3.1 The discharge shall not be comminuted or macerated and shall have passed through screens as specified and or shall not contain a significant quantity of solid matter with a particle size greater than any indicated. All screenings shall be removed from the discharge.

2.3.1 Where a mechanically cleaned screen is installed, a telemetry alarm system shall be installed and maintained so as to give the operator immediate notification of a failure of the screen cleaning mechanism, unless otherwise agreed in writing by Natural Resources Wales. The operator shall take all appropriate measures to return the screen cleaning mechanism to normal operation as soon as reasonably practicable after receipt of notification of the failure.

3.1.1 Emissions and monitoring

3.1.1 Emissions to water

3.1.1 The limits given in schedule 3 table S3.1 shall not be exceeded.

3.1.2 The limits in schedule 3 table S3.1 to which this condition applies may be exceeded where: in any series of samples of the discharge taken at regular but randomised intervals in any period of twelve consecutive months as listed in column 1 of schedule 3A, no more than the relevant number of samples, as listed in column 2 of schedule 3A, exceed the applicable limit for that relevant parameter. For relevant parameters subject to schedule 3C the assessment is based on a fixed calendar year from 1 January to 31 December inclusive.
3.1.2 For the emission limits in schedule 3 table S3.1 to which this condition applies, no sample of the discharge taken at a time when unusual weather conditions are adversely affecting the operation of the waste water treatment works, shall be taken into account in deciding whether or not the emission limit has been complied with.

3.1.2 On any occasion where unusual weather conditions adversely affect the operation of the waste water treatment works, the operator shall use its best endeavours to mitigate that adverse effect.

3.1.2 For any sample of the discharge taken to be considered for the purposes of (a) above, the operator shall notify Natural Resources Wales in writing within 14 days of becoming aware that an emission limit has been exceeded. That notification shall include a full description of the unusual weather conditions and their impact on the operation of the works.

3.1.2 For the emission limits in schedule 3 table S3.1 to which this condition applies, no sample of the discharge taken at a time when abnormal operating conditions are adversely affecting the operation of the waste water treatment works, shall be taken into account in deciding whether or not the emission limit has been complied with.

3.1.2 On any occasion where abnormal operating conditions adversely affect the operation of the waste water treatment works, the operator shall use its best endeavours to mitigate that adverse effect.

3.1.2 For any sample of the discharge taken to be considered for the purposes of (a) above, the operator shall notify Natural Resources Wales in writing within 14 days of becoming aware that an emission limit has been exceeded. That notification shall include a full description of the abnormal operating conditions and their impact on the operation of the works.

3.1.3 The permitted Dry Weather Flow limit in schedule 3 table S3.1 is set at the operator`s planned annual 80% exceeded daily volume discharged. 

3.1.3 For compliance purposes an exceedance shall be recorded for a calendar year only when the limit in effect on 31 December of that calendar year is exceeded by 90% or more of the ‘good’ recorded Total Daily Volumes in that calendar year. 

3.1.3 Until 1 January 2026 

3.1.3 If an exceedance of the Dry Weather Flow limit is recorded in a calendar year then the operator shall, as soon as is practicable, investigate the reasons for the exceedance. 

3.1.3 The operator shall report the reasons for the exceedance to Natural Resources Wales and the steps that it proposes to take to restore compliance. 

3.1.3 An exceedance of the Dry Weather Flow limit shall not be recorded as a failure of the Dry Weather Flow limit in that calendar year if the operator takes appropriate steps to restore compliance. 

3.2.1 Emissions of substances not controlled by emission limits

3.2.1 For the activity A1 referenced in schedule 1, table S1.1 The operator shall take appropriate measures to minimise so far as reasonably practicable the polluting effects of the emissions of substances in the discharge not controlled by emission limits (excluding odour).
3.3.1 Monitoring 

3.3.1 The operator shall, unless otherwise agreed in writing by Natural Resources Wales, undertake the monitoring specified in the following tables in schedule 3 to this permit:

3.3.1 point source emissions specified in tables S3.1 and S3.4;

3.3.1 inlet quality specified in tables S3.1 and S3.4.

3.3.2 The operator shall maintain records of all monitoring required by this permit.

3.3.3 Monitoring equipment, techniques, personnel and organisations employed for the emissions monitoring programme [and the environmental or other monitoring] specified in condition 3.3.1 shall have either MCERTS certification or MCERTS accreditation (as appropriate), where available, unless otherwise agreed in writing by Natural Resources Wales.

3.3.4 Accessible monitoring points shall be provided and maintained to enable the emissions monitoring programme to be carried out at the monitoring points specified in table S3.4 of schedule 3 and shown marked on the site plan in schedule 7. 

3.3.5 The monitoring programme for the parameters subject to schedule 3B shall be:

3.3.5 pre-scheduled to cover a calendar year and the programme recorded before the start of a calendar year sample period; and

3.3.5 spot samples collected at approximately equal intervals during the year, including samples from different days of the week and different times.  Approximately 10% of samples should be outside the normal sampling window which is 9am-3pm, Monday to Friday.

3.3.6 After becoming aware, or following a notification that a sample has not been taken on the schedule 3B Monitoring Programme pre-scheduled date, or is lost, or a result for that sample cannot be reported, the operator shall record the details and reschedule the sample.
3.3.7 The monitoring programme for the parameters subject to schedule 3C shall be: 

(a) pre-scheduled before each calendar year; 

(b) Unless otherwise agreed in writing by Natural Resources Wales, the operator shall submit the monitoring programme for the following calendar year to Natural Resources Wales before the 1st of December; and 

(c) samples must be collected at approximately equal intervals during the year from different days of the week and approximately 10% of samples should be taken at weekends. 
3.3.8   Unless otherwise agreed in writing by Natural Resources Wales, after becoming aware, or following notification that a sample has not been taken on the schedule 3C Monitoring Programme pre-scheduled date, or is lost, or a result for that sample cannot be reported, the operator shall notify Natural Resources Wales of the missed even and the reschedule date as soon as reasonably practicable. 

3.3.9
Effective from the date of installation of EDM monitoring equipment at the Site:The Operator shall take appropriate measures to ensure that the event recorder remains fully operational at all times within the reference period specified in table S3.1. Any failures shall be remedied as soon as reasonably practicable.

3.3.10
(a) Total Daily Volumes shall be calculated from the average of the available ‘good’ 15-minute flow readings taken from midnight to midnight where; 

Total Daily Volume (m3) = {Sum of ‘good’ readings (l/s) / number of ‘good’ readings} x {86,400 (s) /1000}. 

Where there are 87 or more ‘good’ 15-minute flow readings the Total Daily Volume shall be reported as ‘good’, where there are 1 – 86 ‘good’ readings it shall be reported as ‘suspect’ and where there are no ‘good’ readings as ‘missing’. 

(b) The operator shall record all failures of the flow measurement system and any other breaks in the flow record and the reasons for all issues, failures and breaks that lead to missing or suspect Total Daily Volume records and all steps taken to prevent a re-occurrence. 

(c) There shall be no more than 37 days and/or no more than 14 consecutive days with ‘suspect’ or ‘missing’ Total Daily Volumes in a calendar year, unless otherwise agreed in writing by the Natural Resources Wales. 

(d) All 15-minute flow readings shall be flagged as ‘good’, ‘suspect’ or ‘missing’ using an appropriate methodology set out in the operator`s flow monitoring quality management system.
4.1.1 Information

4.1.1 Records

4.1.1 All records required to be made by schedule 3, 4 and 5 to this permit shall:

4.1.1 be legible;

4.1.1 be made as soon as reasonably practicable;

4.1.1 if amended, be amended in such a way that the original and any subsequent amendments remain legible, or are capable of retrieval; and

4.1.1 be retained, unless otherwise agreed in writing by Natural Resources Wales, for at least 10 years from the date when the records were made. 

4.1.2 The operator shall maintain convenient access, in either electronic or hard copy, to the records, plan and management system required to be maintained by this permit. 
4.2.1 Reporting

4.2.1 The operator shall send all reports and notifications required by the permit to Natural Resources Wales using the contact details supplied in writing by Natural Resources Wales.

4.2.2 Within the time period after the end of the reporting period specified in schedule 4 table S4.1 the operator shall, unless otherwise agreed in writing by Natural Resources Wales, submit reports of the monitoring and assessment carried out in accordance with the conditions of this permit, as follows:

4.2.2 in respect of the parameters and monitoring points specified in schedule 4 table S4.1;

4.2.2 [for the reporting periods specified in schedule 4 table S4.1 and] using the forms specified in schedule 4 table S4.2; and

4.2.2 giving the information from such results and assessments as may be required by the forms specified in those tables.

4.2.3 On request, the Operator shall supply Natural Resources Wales with written details of individual spill event(s). 
4.3.1 Notifications

4.3.1 Natural Resources Wales shall be notified as soon as reasonably practicable following detection, within the site of the regulated facility of:

(a) any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution; and

(b) any breach of a limit specified in schedule 3 table S3.1 (including individual exceedances of limits which are covered by condition 3.1.2).

Any other significant adverse environmental effects, which may have been caused by the activity, shall also be notified to Natural Resources Wales as soon as reasonably practicable following detection.

4.3.2 The information provided under condition 4.3.1 shall be supported by sending the information listed in schedule 5 to this permit within the time period specified in that schedule.

4.3.3 Where Natural Resources Wales has requested in writing that it shall be notified when the operator is to undertake monitoring and/or spot sampling specified in schedule [3B/3C], the operator shall inform Natural Resources Wales when the relevant monitoring and/or spot sampling is to take place. The operator shall provide this information to Natural Resources Wales at least 14 days before the date the monitoring is to be undertaken.

4.3.4 Natural Resources Wales shall be notified within 14 days of the occurrence of the following matters, except where such disclosure is prohibited by Stock Exchange rules:

Where the operator is a registered company:

4.3.4 any change in the operator’s trading name, registered name or registered office address; and

4.3.4 any steps taken with a view to the operator going into administration, entering into a company voluntary arrangement or being wound up.

Where the operator is a corporate body other than a registered company:

(c) any change in the operator’s name or address; and

4.3.4 any steps taken with a view to the dissolution of the operator.

4.3.5 For the activity A1 referenced in schedule 1, table S1.1 where the operator proposes to make a change in the nature of the activity by increasing the concentration of, or the addition of, or allowing the introduction of, a substance to the activity to an extent that the operator considers could have a significant adverse environmental effect on the receiving waters, and the change is not permitted by emission limits specified within schedule 3 table S3.1 or the subject of an application for approval under the EP Regulations or under the terms of this permit:

4.3.5 Natural Resources Wales shall be notified in writing at least 14 days before the increase or addition or allowing the introduction; and

4.3.5 the notification shall contain a description of the proposed change.

4.3.6 For the activity A1 referenced in schedule 1, table S1.1 the operator shall inform Natural Resources Wales in writing of any change, or proposed change, to the population equivalent such as would make a material change to the application of the Regulations and shall, on request, inform the Natural Resources Wales in writing of the actual population equivalent. 

4.4.1 Interpretation

4.4.1 In this permit the expressions listed in schedule 6 shall have the meaning given in that schedule.

4.4.2 In this permit references to reports and notifications mean written reports and notifications, except where reference is made to notification being made “as soon as reasonably practicable”, in which case it may be provided by telephone.
Schedule 1 – Operations 
	Table S1.1 Activities

	Activity reference
	Description of activity
	Limits of specified activity

	A1
	Discharge of secondary treated sewage effluent via FE Discharge Point
	N/A

	A2
	Discharge of storm sewage via Storm Discharge Point
	N/A


Schedule 2 – Waste types, raw materials and fuels

Schedule 2 not in use.

Schedule 3 – Emissions and monitoring
	Table S3.1 Point Source emissions to water (other than sewer) – emission limits and monitoring requirements

	Effluent and discharge point
	Parameter  
	Limit (including unit)
	Reference Period
	Limit of effective range
	Monitoring frequency
	Compliance Statistic

	A1 Secondary treated sewage via FE Discharge Point
	Dry weather flow
	792 m3/day


	Total daily volume
	N/A                                                                
	Continuous
	Condition 3.1.5 and 3.3.10 applies

	
	15-minute instantaneous or averaged flow
	No limit set. Record as l/s
	15 minute
	N/A
	Continuous
	N/A

	
	ATU-BOD as O2
	9.5 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table

(Conditions 3.1.2 and 3.1.3 apply)

	
	ATU-BOD as O2
	50 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Maximum

(Condition 3.1.3 applies)

	
	Ammoniacal nitrogen (expressed as N)
	3 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table

(Conditions 3.1.2 and 3.1.3 apply)

	
	Ammoniacal nitrogen (expressed as N)
	20 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Maximum

(Condition 3.1.3 applies)

	
	Suspended solids (measured after drying at 105oC)


	14 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table

(Conditions 3.1.2 and 3.1.3 apply)

	
	Suspended solids (measured after drying at 105oC)


	75 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Maximum

(Condition 3.1.3 applies)

	
	Visible oil or grease
	No significant trace present so far as is reasonably practicable
	Instantaneous (visual examination )
	N/A
	N/A
	No significant trace

(Condition 3.1.3 applies)

	
	ATU-BOD as O2  (UWWTR)
	Minimum of 70 % removal compared to influent
	24 hour composite
	To be compliant a sample has to meet the 70% removal standard or the 25 mg/l limit not both 
	As specified in schedule 3C 
	Look up table

(Conditions 3.1.2 and 3.1.4 apply) 

	
	ATU-BOD as O2  (UWWTR)
	25 mg/l
	
	
	
	

	
	COD as O2 (UWWTR)
	Minimum of 75 % removal compared to influent
	24 hour composite
	To be compliant a sample has to meet the 75% removal standard or the 125 mg/l limit not both 
	As specified in schedule 3C
	Look up table

(Conditions 3.1.2 and 3.1.4 apply) 

	
	COD as O2 (UWWTR)
	125 mg/l
	
	
	
	

	A2 Storm sewage via Storm Discharge Point

	Discharge start and end times 
	N/A


	N/A


	N/A


	Whenever a discharge occurs
	N/A



	
	Block counted spills 
	N/A
	1st January to 31st December inclusive 
	N/A
	15 minutes
	N/A

	
	Event recorder status operational 
	N/A
	N/A
	N/A
	15 minutes
	N/A


	Table S3.2 Discharge points

	Effluent Name
	Discharge Point
	Discharge point NGR
	Receiving water

	A1 Secondary treated sewage effluent 
	FE Discharge Point
	ST 11067 79713
	Nant Dowlais

	A2 Storm sewage
	Storm Discharge Point
	ST 11097 79787
	Nant Dowlais


	Table S3.3 Storm sewage discharge settings

	Effluent and discharge point 
	Description of discharge
	Overflow setting l/s
	Maximum size of solid matter
	Screen aperture

size
	Minimum screen capacity flow l/s
	Minimum  storage capacity m3 (on-line)

	A2 Storm sewage via Storm Discharge Point
	Storm sewage
	36.3 
	No greater than 6 mm in more than 1 dimension


	6 mm x 6 mm 
	The screen shall be designed to cope with all flows up to and including the 1 in 5 year storm return period, as a minimum
	N/A

 


	Table S3.4 Monitoring points

	Effluent and discharge point
	Monitoring type
	Monitoring point NGR
	Monitoring point reference

	Secondary treated sewage effluent
	Inlet sampling
	ST 11044 79801
	Influent sampling point

	
	Final Effluent sampling
	ST 11050 79728
	FE sampling point

	
	Flow to full treatment monitoring point
	ST 11044 79801
	Mcerts Monitoring Point

	Storm sewage via Storm Discharge point

	Storm Effluent sampling
	ST 11043 79791
	Storm Sample Point

	
	Event duration monitoring
	ST 11043 79791
	EDM Monitor


Schedule 3A - Look up table

	Look up table

	Number of samples taken in any period of 12 months
	Maximum number of samples permitted to exceed limit for given parameter

	4–7  
	 1

	8–16
	 2

	17–28 
	 3

	29–40 
	 4

	41–53  
	 5

	54–67  
	 6

	68–81  
	 7

	82–95 
	 8

	96–110 
	 9

	111–125  
	 10

	126–140  
	 11

	141–155  
	 12

	156–171  
	 13

	172–187 
	 14

	188–203  
	 15

	204–219  
	 16

	220–235  
	 17

	236–251 
	 18

	252–268 
	 19

	269–284  
	 20

	285–300  
	 21

	301–317 
	 22

	318–334  
	 23

	335–350 
	 24

	351–365 
	 25


Schedule 3B - OSM tier 3 sampling frequency

	Parameter
	‘Normal frequency’ of samples per year
	Reduced Sampling frequency after 12 consecutive months of numeric permit compliance, samples per year or pro rata over the remainder of a year
	On numeric limit failure return to normal frequency as soon as reasonably practicable, samples per 12 months
	Out of hours samples

	Sanitary


	24
	12
	24
	For 24 samples 2 out of hours samples per annum

	Non sanitary


	12
	12
	12
	For 12 samples 1 out of hours sample per annum


Schedule 3C – Urban Waste Water Treatment Regulations sampling frequency

	Population equivalent
	Samples per year
	Reduced sampling frequency after a year without an UWWTR exceedance or failure, samples per year
	Following an UWWTR exceedance or failure return to the higher frequency in the year that follows, samples per year

	2,000 to 9,999

	12
	4
	12

	10,000 to 49,999

	12
	N/A
	N/A

	50,000 or over

	24
	N/A
	N/A


Schedule 4 – Reporting

Parameters, for which reports shall be made, in accordance with conditions of this permit, are listed below.

	Table S4.1 Reporting of monitoring data

	Parameter
	Monitoring point reference
	Reporting period
	Period begins

	Dry Weather Flow (daily flows total)
	Mcerts Monitoring Point
	Annually

Report to be submitted within 2 months of the end of the calendar year
	1 January

	15-minute flow
	Mcerts Monitoring Point
	Reports to be provided to Natural Resources Wales upon request 

Report to be submitted within 28 days unless otherwise specified in writing by Natural Resources Wales
	Upon request by Natural Resources Wales

	UWWTR  - ATU-BOD as O2, COD as O2, 
	FE Sampling point and Influent sampling point 
	Monthly

Report to be submitted within 28 days
	1st of month

	Operator Self Monitoring - ATU-BOD as O2, ammoniacal nitrogen (expressed as N), suspended solids (measured after drying at 105oC), 
	FE Sampling point
	Quarterly

Report to be submitted within 28 days
	1st of month

	Operator Self Monitoring 
	FE Sampling point
	Annually

Report to be submitted within 2 months of the end of the calendar year
	1 January

	CSO performance, including adjusted number of total spills


	EDM Monitor
	Annually

Report to be submitted within 2 months
	1 January

	Duration of total spills


	EDM Monitor
	Annually

Report to be submitted within 2 months
	1 January

	Event recorder status operational


	EDM Monitor
	Annually

Report to be submitted within 2 months
	1 January

	Storm sewage discharge start and end times


	EDM Monitor
	Reports to be provided to Natural Resources Wales upon request 
	As specified by Natural Resources Wales


	Table S4.2 Reporting forms

	Parameter
	Reporting format

	Dry Weather Flow (daily flows total)
	WISKI electronic format specified by Natural Resources Wales

	15-minute flow
	WISKI electronic format specified by Natural Resources Wales

	UWWTR – ATU-BOD as O2, COD as O2, 
	Electronic format specified by Natural Resources Wales

	OSM - ATU-BOD as O2, ammoniacal nitrogen (expressed as N), suspended solids (measured after drying at 105oC), 
	Quarterly - Electronic format specified by Natural Resources Wales 

	Operator Self Monitoring summary report
	Annually - Summary report of compliance with the monitoring programme specified in Table 3.1 and schedule 3B in a format specified by Natural Resources Wales  

	Storm sewage discharge start and end times
	Form as agreed in writing by Natural Resources Wales 

	Event recorder status
	[Annual and/or bathing water summary report] or other form as agreed in writing by Natural Resources Wales

Percentage of time in the recording period that event duration monitoring equipment is operational

	Investigation into the operation of the overflow
	Electronic format as agreed in writing by Natural Resources Wales. 


Schedule 5 – Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A

	Permit Number
	AE2021601

	Name of operator
	

	Location of Facility
	 Rhydlafar, WwTW, Rhydlafar, Cardiff, 

	Time and date of the detection 
	


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques,  accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 7 days of detection unless otherwise agreed in writing by the Natural Resources Wales.



	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released/type or nature of sewage released
	

	Best estimate of the quantity or rate of release of substances and/or duration of discharge
	

	Best estimate of the environmental impact of the discharge
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a limit specified in schedule 3 table S3.1 (including individual exceedances of limits which are covered by condition 3.1.2)



	The information specified below is to be notified to Natural Resources Wales as soon as reasonably practicable following detection.

	Monitoring point reference/ source
	

	Self monitoring regime (where relevant)
	e.g. OSM/UWWTR



	Type of failure 
	e.g. LUT failure/LUT exceedance/upper tier/other

Drafting note: insert the self monitoring regime(s) and type(s) of failure relevant to the permit. Change to black text and retain ‘e.g.’.

	Date of sample/event
	

	Parameter
	

	Result and units
	

	Limit and units
	


Part B – to be submitted as soon as reasonably practicable unless otherwise agreed in writing by Natural Resources Wales

	Any more accurate information on the matters for notification under Part A.
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident/breach/exceedance
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	


	Name*
	

	Post
	

	Signature
	

	Date
	


* authorised to sign on behalf of the operator

Schedule 6 – Interpretation 
“accident” means an accident that may result in pollution.

"annually" means once every year.

“application” means the application for this permit, together with any additional information supplied by the operator as part of the application and any response to a notice served under Schedule 5 to the EP Regulations.

For the activities A1 to A2 referenced in schedule 1, table S1.1 “appropriate measures” for the purposes of the emission of substances not controlled by emission limits condition (condition 3.2.1) do not require the operator to undertake treatment to a level beyond that specified in schedule 1 table S1.1, or to carry out routine monitoring for substances not controlled by emission limits.

“ATU-BOD as O2” means the biochemical oxygen demand (measured after 5 days at 20oC with nitrification suppressed by the addition of allylthiourea).

“COD as O2” means the chemical oxygen demand (measured using the standard dichromate procedure).

“emissions of substances not controlled by emission limits” means emissions of substances to air, water or land from the permitted activities, which are not controlled by an emission limit.

“EP Regulations” means The Environmental Permitting (England and Wales) Regulations SI 2016 No.1154 and words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.

"event recorder" a recorder which records the start time and  end time of individual overflow events.

“MCERTS” means the Natural Resources Wales’ Monitoring Certification Scheme.

“minimum screen capacity flow” means the minimum flow passed through the screens to the outfall when the screen bypass operates. 

“monitoring frequency” as used in Table S3.1 in the context of event duration monitoring is the temporal interval at which a change in state between no discharge and discharge is to be detected.

“Natural Resources Wales” means the Natural Resources Body for Wales established by article 3 of the Natural Resources Body for Wales (Establishment) Order 2012. The Natural Resources Body for Wales (Functions) Order 2013 transferred the relevant functions of the Countryside Council for Wales, and functions of the Environment Agency and the Forestry Commission in Wales to the Natural Resources Body for Wales.

“overflow” for the purposes of schedule 7, overflow means the weir or orifice or other control which directs excess flow away from the continuation sewer when the flow exceeds the overflow setting due to rainfall and/or snowmelt.

“overflow setting” means the minimum flow passed forward to the continuation sewer when the overflow operates.

"quarter" means a calendar year quarter commencing on 1 January, 1 April, 1 July or 1 October.

“significant pollution” means a high level impact incident as indicated by NRW incident classification system.
“significant spill” any spill that has not been demonstrated to have been, or measured as being, less than 50 m3 in volume.

“block counted spill” one or more overflow events within a period of 12 hours or less will be considered to be one spill, one or more overflow events extending over a period of greater than 12 hours up to 36 hours will be considered to be 2 spills. Each subsequent 24 hour duration counts as 1 additional spill and the whole of the 24 hour block is included. 

“unusual weather conditions” includes, but is not limited to:

· low ambient temperatures, or the freezing of mechanical equipment in the works;

· significant snow deposits;

· tidal or fluvial flooding;

· weather conditions causing unforeseen loss of power supply to the sewage treatment that could not be ameliorated by the reasonable provision and operation of standby generation facilities.
“Urban Waste Water Treatment (England and Wales) Regulations 1994 (UWWTR)” means Urban Waste Water Treatment (England and Wales) Regulations 1994 SI 2841and the words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.

“year” means calendar year ending 31 December.

Schedule 7 – Site plan
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