Schedule 5 - Notification

These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EPR.

Part A

| Permit Number | EPR/AB3595FF |
| --- | --- |
| Name of operator | Runtech Ltd |
| Location of Facility | Port Talbot Steel Works, Port Talbot, SA13 2NG |
| Time and date of the detection | 16:45pm 25.10.2024 |

| (a) Notification requirements for any activity that gives rise to an incident or accident which significantly affects or may significantly affect the environment |  |
| --- | --- |
| To be notified Immediately |  |
| Date and Time of the event | 16:45 25.10.2024 |
| Reference or description of the location of the event | Location of monitor at Scarfing permit office |
| Description of where any release into the environment took place | N/A |
| Substances(s) potentially released | Particulate |
| Best estimate of the quantity or rate of release of substances | N/A |
| Measures taken, or intended to be taken, to stop any emission | N/A |
| Description of the failure or accident. | The monitor failed to collect the data since the last download in July. |

| (b) Notification requirements for the breach of a permit condition |  |
| --- | --- |
| To be notified immediately |  |
| Emission point reference/ source | AS1 |
| Parameter(s) | Particulate Matter |
| Limit | 10mg/m3 as an hourly average, no single reading shall be more than 3 times this limit |
| Measured value and uncertainty | N/A |
| Date and time of monitoring | 16:45pm 25.10.2024 |
| Measures taken, or intended to be taken, to stop the emission | N/A |

| Time periods for notification following detection of a breach of a limit |  |
| --- | --- |
| Parameter | Notification period |
| Particulate Matter | Immediately |

| (c) In the event of a breach of permit condition which poses an immediate danger to human health or threatens to cause an immediate significant adverse effect on the environment: |  |
| --- | --- |
| To be notified immediately |  |
| Description of where the effect on the environment was detected | N/A |
| Substances(s) detected | N/A |
| Concentrations of substances detected | N/A |
| Date of monitoring/sampling | N/A |

Part B to be supplied as soon as practicable

| Any more accurate information on the matters for notification under Part A. |  |
| --- | --- |
| Measures taken, or intended to be taken, to prevent a recurrence of the incident | Our Technical Service (Envea Uk Ltd) have advised to wipe all current data clear from the monitor and they believe that this will fix the problem. They also suggested that we download monthly going forward instead of quarterly as we have been doing. We also are going to, initially for the first month, download the data weekly to ensure it is working correctly and collecting the data. If there is still a problem then we can act that much sooner to fix it. Plus we will also inform NRW weekly of our progress. We will wipe the logs clear today 25.10.24 and carry out our first download next week. Plus see attached email from Envea confirming the above. |
| Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission | As above |
| The dates of any unauthorised emissions from the facility in the preceding 24 months. | N/A |

| Name* | Paul North |
| --- | --- |
| Post | Quality & Environment Manager |
| Signature | P North |
| Date | 28.10.24 |

* authorised to sign on behalf of the operator