Pumping Station Emergency Discharge Key Protection Measures

| Site name: |  | SPS at Trefriw WwTW 01017 |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Permit Number and Activity Reference: |  | CG0084201 |  |  |  |
| Version number and Date |  | Version 1 – 26th September 2024 |  |  |  |
| Pumps: | Duty pump(s) installed and maintained in working order: |  |  | Yes |  |
|  | Standby pump(s) installed and maintained in working order : |  |  | Only one pump |  |
|  | Automatic standby pump activation on duty pump failures other than power failure: |  |  | No |  |
|  | Pump reactivation as soon as is practicable when power restored after power failure: |  |  | Pumps |  |
|  | Over pumping facility installed and maintained for use if the installed pumps are inoperative: |  |  | None |  |
|  | Tanker access provided and maintained at an appropriate location to enable removal of sewage by tanker when necessary: |  |  | Tanker access is available to site Pipes need to be set up to reach the raised treatment * |  |
| Maintained 24 hour response telemetry alarm system to; | Notify Operator: |  |  |  |  |
|  | Failure or breakdown of the pumping station |  |  |  | Yes |
|  | Overflow operating |  |  |  | Yes |

| Alarm response | Response: Take all reasonable remedial measures to return the pumping station to normal operation. | Attended out of hours |
| --- | --- | --- |
|  | Response time: As soon as reasonably practicable after receipt of warning of failure or breakdown of the pumping station | 2 hrs in hours / 4 hrs out of hours |
| Standby power provision: | Mobile generator point. Install and operate a mobile generator as soon as is reasonably practicable in the event of an electrical failure | No plug in point, would need to be wired in |
|  | Permanent standby generator installed and maintained in good working order and activated in the event of an electrical power failure. | No |
|  | Duplicate power supply provided, and activated in the event of an electrical power failure | No |
| Emergency storage capacity Hours @ DWF*: | Storage capacity, equivalent to a total of at least x hours of the dry weather flow* (“DWF*”), shall be provided above the normal top operating level in dry weather and below the level of the overflow. | Approx.. 7 hrs. (Prior to the 2010 DWF Modification, DWF was 199 m3/day so 7 hours would be 58 m3) |
| Design dry weather flow limit | The figure proposed here should be based on the projected PG + I + E at your proposed design horizon: | Flow to site is pumped, when pump runs it pumps 23 l/s. Data from telemetry during a dry period of seven days gives a mean flow of 3.901 l/s |
| Emergency storage capacity m3 | Minimum storage volume provided above the normal top operating level in dry weather and below the level of the overflow | Only in the wet well, unable to access this to confirm volume. * |

| Screening: | Screen fitted | None |
| --- | --- | --- |
|  | Screen type | N/A |
|  | Screen aperture size | N/A |
| Any other key protection measures (e.g. enhanced target response times, links and dependencies to other pumping stations such as pump inhibits and tankering at upstream pumping stations in an emergency): | * Alternatively, tankers could draw from the Trefriw Main SPS 00584 which is the SPS pumping flows forward for treatment or storage there could be utilised. If there was a power outage across the whole of Trefriw then with negotiation with NRW spills could occur from there instead. |  |