
[image: This is the preferred use of the logo - please refer to the brand guidelines for more guidance or speak to Marketing]

Pwllfawatkin HWRC
Rhy Dy Fro,
Pontradawe,
Swansea,
SA8 4RX


Fire Prevention Plan
10/03/2018








1.	Introduction
This Fire Prevention Plan (FPP) has been written following consultation with the following guidance documents:
· ‘Fire Prevention Plans: environmental permits’ (version 3), the Environment Agency, 29 July 2016
· Fire Prevention & Mitigation Plan Guidance –Waste Management Guidance Note 16 version 2 2017
· Waste Industry Safety and Health Forum (WISH) – WASTE 28 Reducing fire risk at waste management sites issue 2 April 2017
The FPP forms part of the sites management system and sets out the fire prevention measures and procedures in place on ‘the site’. This is a standalone document, however it may be useful to read this in conjunction with the Fire Risk Assessment on site and the Emergency Management Plan in appendix 3 of this document.
This FPP and the fire prevention measures specified within it have been designed to meet these three main objectives:
· Minimise the likelihood of a fire happening
· Aim for a fire to be extinguished within 4 hours
· Minimise the spread of a fire within the site and to neighbouring sites
All site staff shall be made aware of the location of this FPP and be able to access it at all times, including during an incident. Site staff and contractors working on site shall be made aware of the contents of the FPP so that they know what they must do:
· To prevent a fire occurring
· During a fire if one breaks out
Regular fire drills are carried out to test how well the plan works and ensure staff understand what to do. These drills will be undertaken 6 monthly as a minimum.

2.	Site activities
Pwllfawatkin  HWRC is a civic Amenity Centre. Situated in Rhyd Y Fro and accepts household waste on behalf of NPTCBC
 ‘The site’ accepts the following combustible wastes: 
Mixed waste (containing any combustible wastes)
· Paper and cardboard
· Mattress
· Plastics and UPVC
· Rubber (whole tyres, baled tyres, tyre shred, crumb and fibre
· Wood (including planks, boards, sawdust, shavings, logs, firewood or chips, crates, pallets, casts or barrels)
· Rags and textiles
· Scrap metal
· Municipal residual waste
· Waste electrical and electronic equipment such as fridges, computers and televisions containing combustible materials such as plastic
· Green Waste
· Paints
· Bulky waste

Sensitive receptors within 1 km of the site are identified in Table 1 and maps in Drawing 1
Table 1. Key receptors within 1 km of site.

	No
	Receptor
	Category
	Distance
M
	Direction
	Prevailing
wind

	1
	Houses
	Residential
	1000
	E
	Low


	2
	landfill
	Buisness
	50
	N
	High

	3
	A473
	Road
	1000
	E
	Low



3.	Managing common causes of fire
The possible causes of a fire at ‘the site’ have been identified In the fire risk assessment and measures in place to reduce the risk are detailed below.
3.1	Arson
To prevent or reduce risk of arson, the site has a parimiter fence with locked gates.
3.2	Plant and equipment
There is no plant at Pwllfawatkin HWRC
3.3	Electrical faults
Fixed electrics are installed by a qualified electrician certified by NICEIC and are inspected 3 yearly. Portable appliances are tested annually.
3.4	Smoking materials
‘The site’ operates a no smoking policy, has a designated smoking area situated at the the main gates away from combustible materials to prevent accidental ignition.
3.5	Hot works
Any hot works such as welding or cutting undertaken by staff or contractors are done so with a suitable risk assessment and safe working procedure in place. Hot works undertaken by contractors are done so under a Permit to Work and a fire watch is set for a minimum of 30 minutes after work has been completed with a final check after 60 minutes.
3.6	Industrial heaters
Industrial heaters are kept away from combustible materials, must not be covered and are switched off during non-operational hours. They are regularly maintained and inspected annualy.
3.7	Hot exhausts
No plant on site to monitor.
3.8	Other sources of ignition
Sources of ignition, such as naked flames are kept at least 6m away from combustible and flammable materials.
3.9	Batteries 
To prevent the risk of a short circuit any batteries disconnected and removed, will be stored appropriatley following the Safe Working Procedures, before they are stockpiled for collection.
3.10	Leaks and spillages of oils and fuels
Vehicles using or servicing site are subject to regular inspection and maintenance as identified in section 3.2.
Waste Oils are stored within bunded tanks and spill containment equipment is stored adjacent to these areas.
3.11	Build-up of loose combustible waste, dust and fluff
The site is inspected daily for build-up of loose combustible waste, dust and fluff. Cleaning is undertaken daily.
3.12	Reactions between incompatible wastes/materials
All wastes are inspected on arrival, where possible, or inspected by an operative as they are being disposed by MOP (Memebr of Public) Any identified non-conforming wastes and/or incompatible wastes will be separated and quarantined immediately in an area with sealed drainage where necessary.
3.13	Hot loads
Hot loads identified prior to tipping will be placed within a quarantine area immediately. Any hot loads that have been deposited will either be removed to a quarantine area where safe to do so, or any combustible wastes adjacent to the deposited hot load will be removed to prevent spread. 

4.	Self-combustion
To minimise the risk of self-combustion storage times, pile volumes and heights, and temperatures of wastes are managed.
4.1	Storage time
All combustible wastes are stored for less than 3 months, see the table in Appendix 1 for storage times of each material.
Extra measures to prevent self-combustion include:
· Ensure wastes are not stored over long periods
· Reduced pile sizes.
4.2	Temperature control
Heat is controlled to prevent self-combustion by:
· Start at morning shift and End of shift fire watch and checks on waste, see appendix 2 site installation checks
· Waste limited to a maximum of 3 months on site
· All waste in small quantities mainly in containers
5.	Waste piles
The majority of wastes are in containers with limited number stored loose.
Pile sizes of combustible wastes are managed to help prevent self-combustion and to limit the scale of a fire if one breaks out. The table in Appendix 1 identifies the combustible waste types accepted at ‘the site’, the average daily tonnage received and how those wastes are stored. All piles are kept to a maximum of 4 metres in height and 20 metres in length/width.  
Pile sizes are minimised and wastes are stored in their largest form where possible.

6.	Preventing fire spread
Separation distances, containers have been used to prevent the risk of a fire spreading. The table in Appendix 1 and Drawing 2 identifies the separation distances between wastes where relevant.
6.1	Separation distances
All materials are either in containers, apart from a very small quality of UPVC frames stored 3m away from buildings and other materials are removed every week keeping the quantity stored low.
7.	Quarantine area
The quarantine area will be used in the event of a fire to either hold burning wastes or to hold unburnt wastes to isolate and prevent them catching fire, this is shown on the site plan drawing 2. Skips can be moved by FCC’s fleet of vehicles, which will be available within 30mins on working days but will also be available out of hours. 
A separate quarantine area for non-conforming wastes is also on site for small quantities of waste.
8.	Detecting and supressing fires
8.1	Detecting fires
Regular checks, Morning and end of shift checks (see appendix 2), smoke detectors in the cabins and fire watch when hot works are carried out
8.2	Supressing fires
Fire extinguishers, fire blankets, staff trained
9.	Firefighting techniques
The site is operated to allow for active firefighting. Appropriate resources are available to fight a fire including:
· Trained operators
· Water supply
· Finances
Firefighting techniques will include some or all of the following:
· Applying water to cool unburned material and other hazards
· Separating burning material from the fire to quench it
These actions will be taken under supervision from the fire and rescue service.
This Fire Prevention Plan will be supplied to the local Fire and Rescue Authority (FRA).
FRA contact details: NPT 01639 636107
10.	Water supplies
There is available water supply from within the adjacent landfill
11.	Managing fire water
Fire water will be contained to minimise pollution from fire water as far as reasonably practicable.  The site is engineered to ensure water is directed to the interceptor before leaving the site.  The site also has spill barriers available to help direct water if needed to the interceptor.
12.	During and after an incident (contingency measures)
In the event of a fire incoming wastes will be stopped and where required diverted to alternative sites. The alternative sites are:
· Cymmer
· Briton Ferry
Residents that may be affected by a fire will be contacted if considered necessary, contact details are found within the Emergency Management Plan (Appendix 3).
Once safe to do so contaminated materials and fire water will be removed from site and disposed of by authorised parties.
The site will then be inspected and all necessary rectifications made to make the site safe prior to any operations commencing. This will be done in agreement with the sites Health and Safety Advisor, Environment Advisor and Engineering department. 
13.	Emergency services 
A copy of this fire prevention plan will be given to the local Fire and Rescue Authority (FRA) for their information and comments.
Safe access for fire and rescue services will be achieved by maintaining routes for fire engines and access points around the site perimeter through good site layout as indicated in drawing 2.
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Appendix 1 Waste types and storage

	Waste type
	Daily tonnage received / processed (approx.)
	Total stored at any one time (tonnes)
	Form 
	Max. storage time (days)
	Location
	Max. volume of waste pile (m3)
	Maximum size of waste pile
	Minimum separation (fire break) (m)

	
	
	
	Unprocessed; shredded; baled
	>150mm; 30-150mm; <30mm
	
	
	
	Length (m)
	Width (m)
	Height(m)
	

	Wood
	0.5
	8
	unprocessed
	
	7
	Yard
	40yd container
	
	
	
	

	Tetra Pack
	0.01
	1
	unprocessed
	
	annual
	yard
	1 bank 
	
	
	
	


	Plastics
	0.5
	5
	unprocessed
	
	7
	yard
	40yd container
	
	
	
	

	UPVC
	0.2
	1
	unprocessed
	
	14
	Yard
	8
	2
	2
	2
	

	Carpet
	0.1
	3
	unprocessed
	
	28
	yard
	25yd container
	
	
	
	


	Bulky waste
	1
	15
	unprocessed
	
	7
	yard
	40yd container
	
	
	
	

	Municipal residual waste
	1
	8
	unprocessed
	
	7
	yard
	40yd container
	
	
	
	

	Scrap
	0.5
	7
	unprocessed
	
	14
	yard
	40yd container
	
	
	
	

	SDA
	0.5
	2
	unprocessed
	
	7
	yard
	40yd container
	
	
	
	

	LDA
	0.5
	3
	unprocessed
	
	7
	yard
	40yd container
	3
	2
	3
	

	Batteries
	0.1
	1
	unprocessed
	
	28
	Dolafs (1000L * 2)
	2
	
	
	
	

	Gas bottles
	0.1
	1
	unprocessed
	
	28
	cage
	8
	2
	2
	2
	

	Fridges
	0.1
	2
	unprocessed
	
	14
	yard
	ISO container
	
	2
	2
	3m*2m*3m separated by brick walls

	Paints
	0.1
	1
	unprocessed
	
	28
	shed
	Dolaf (1000L * 2)
	
	
	
	

	Green
	0.1
	5
	unprocessed
	
	14
	yard
	25yd container
	
	
	
	

	oils
	0.1
	5
	unprocessed
	
	1500l
	yard
	1500lt Oil banks
	
	
	
	

	Paper
	0.2
	1
	unprocessed
	
	7
	shed
	1000L Wheelie bins * 4
	
	
	
	

	Card
	0.5
	6
	unprocessed
	
	7
	yard
	40 yd container
	
	
	
	

	Textiles
	0.3
	1
	unprocessed
	
	7
	yard
	Clothes banks * 2
	
	
	
	

	Beds
	0.1
	0.5
	unprocessed
	
	7
	shed
	12
	3
	2
	2
	Contained shed 3m*2m*3m separated by brick walls

	Hardcore
	0.5
	10
	unprocessed
	
	28
	yard
	40yd container 
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Appendix 2 Installation checks

	Site:                                        Pwllfawatkin


	Inspector:

	
	Date:

	Signature:

	Position:
	Permit No: EPR/HP3198FD




	Daily
Installation check and details
	Initial
	Comments
	Action
	Close out

	Weather conditions
	
	
	
	

	Environmental Incidents 
Any incidents to be put on safegaurd

	
	
	
	

	Spill kits
	
	
	
	

	Drainage
	
	
	
	

	Interceptor

	
	
	
	

	Containers
Damage/Leaks
	
	
	
	

	Bays/storage areas
Damage
	
	
	
	

	Security
Fencing
	
	
	
	

	Permitted waste quantities adhered too
	
	
	
	

	Non permitted/non conforming waste 
	
	
	
	

	Fire checks                            AM

                                              PM
	
	
	
	

	Chem Safe
Storage secure, locked
Inventory correct
	
	
	
	

	Signage
Including site notice board
	
	
	
	

	Litter

	
	
	
	

	Odour 
perimeter and receptor      AM                       
                                          PM              Any Complaints – Safeguard                                       
	
	
	
	

	Dust

	
	
	
	

	Mud

	
	
	
	

	Pests

	
	
	
	

	Vehicles leaving site
Clean, free from mud/dirt etc, all waste contained
	
	
	
	

	Comments:
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1.0	EMERGENCY CONTACT DETAILS

· Site Address

FCC Environment
Pwllfawatkin HWRC
Rhyd Y Fro
Pontradawe
Swansea
      SA84RX

· Operational Hours :-  Monday – Sunday 09:00 – 17:00

· Important Contacts

	Name
	Position
	Telephone
	Response Time
	Contacted
[] [Time]

	Emergency Services Numbers

	Emergency Services
	
	999
	
	

	Police
	
	999
	10 Mins
	

	Ambulance
	
	999
	10 Mins
	

	Morriston Hospital

	
	01792702222
	20 min 
	

	Fire Station Direct
	
	0370 60 60 699
	
	

	FCC Site Office Numbers

	Reception
	
	01269824887
	 Immediate 
	

	Fax
	
	01269824895
	 Immediate
	

	
	
	
	
	

	FCC Site Management

	Darren Hemming
	Contract Manager
	07747638830
	45 mins
	

	Michael Adams
	Site Supervisor
	07718666396
	30 Mins
	

	Mike Stass
	Regional Operations Manager
	07769640971
	Two Hour
	

	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	

	
	
	
	
	

	

	
	
	
	
	

	FCC Site Operatives

	
Paul Bennett
Simon Dunn
Peter Roberts

	
HWRC
HWRC
HWRC

	
	
	

	Other FCC Contacts

	FCC
	24 Hour Emergency Number
	01302 553461
	
	

	FCC Head Office
	Northampton
	01604 826200
	
	

	FCC Head Office
	Doncaster
	01302 303030
	
	

	Paul Stokes
	Group SHE Manager
	07833 176978
	
	

	Mitch Gibson
	H&S Advisor
	07765 866309
	
	

	Mike Snell
	General manager External Affairs
	07980 780765
	
	

	Claire Favier-Tilston
	Company Secretary
	01604 826264
	
	

	Paul Marsh
	Estates Manager
	07785 382047
	
	

	Nicola Mirza
	 FCC Sales
	07767 618817
	
	

	
	
	
	
	

	Contractors

	JCB Holts
	 
	01639 813871
	
	

	T C Harrison
	
	0114 2329809
	
	

	Samatrex
	Paul
	07969 305235
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	Regulatory Authorities

	Resources Wales
	Emergency Number
	0800 807 060
	
	

	
	
	
	
	

	HSE
	Cardiff Office
	02920 263 120
	
	

	NPTC
	Council
	01639 686868
	
	

	Local Liaison Contacts

	Parish Councils

	
	
	
	
	

	Residents

	
	
	
	
	

	Neighbouring Business

	
	
	
	
	

	
	
	
	
	

	Utility Companies

	 [Water]
	DWR 
	0800 052 0130
	
	

	 [Electric]
	SWALEC
	0800 052 0400
	
	

	 [Telephone]
	BT
	0800 800152
	
	

	

	
	
	
	
	

	
	
	
	
	







01423 885 959
- more info »

2.0	PURPOSE

The purpose of this document is to:

· comply With the sites permit ,
· minimise the risk of significant environmental and Health and Safety consequences from certain emergencies,
· ensure that all staff are aware of the procedures in the event of a major incident, and
· Identify the types of incidents that can occur at site and the actions to take in the event of a major incident. 

3.0	RESPONSIBILITY

It is the responsibility of the Contract Manager or equivalent to ensure that:

· All Incident Controllers have undertaken an FCC training course
· All Incident Controllers have been inducted/trained on this plan, and
· The requirements of this document are adhered to.

The decision to alert the emergency services will be taken by the Incident Controller who is first aware of an incident. If an incident occurs out of working hours, an external party may make this decision. However, this plan is to be adhered to at all times. 

The Incident Controller who was first made aware of the event will always take the control of any major incident. 

The identity of the Incident Controller may change in which case a formal hand over and communication with the emergency services will be necessary. The Incident Controller will assume responsibility, command and liaison with the emergency services at all times.

In the event of a fire the incident controller has the following roles / responsibilities;

· To assist With the evacuation process by checking a specific area, if safe to do so

· No Incident Controller is expected to place them self in danger, they should check their allocated area swiftly then report to the assembly point

· If necessary, once the emergency has been made safe and re-entry is confirmed the Incident Controller reports any issues that impacted on the effectiveness of the evacuation procedure to the site manager.

· NB investigating the cause of the alarm activation is carried out to avoid unnecessary calls being made to the fire service. While this is the duty of designated incident controller; they are NOT TO PUT THEMSELVES AT RISK

NB: If the fire service is called, the Senior Fire Officer present is legally responsible for the containment of the fire and the safety of all those potentially affected by it. Hose water run-off containment is the responsibility of the site. 

All accidents and near misses must be reported no matter how trivial as per the 
Accident/Incident Procedure IMS-PRO-013


4.0	DEFINITION

A major incident is an event or events that call for assistance or action beyond normal operational plans of the site, i.e. events that require external aid in fire fighting, police or ambulance services. 

Any occurrence on site that threatens the safety of people on site, off site, the surrounding premises, neighbours, houses, the general public or the environment, constitutes a major incident

For further details in controlling environmental impacts the site’s Environmental Aspects Risk Assessment should be reviewed.

5.0	COMMUNICATION

Communication during an emergency should be established at the main site office where possible. 

In the event of communication is required between external parties such as members of public, members of the press, the external communications managers should be contacted (Mike Snell) and all communications dealt With by him or is deputy and not at a site level

Communication should also be established with any applicable neighbours along With any enforcing body to inform them of the emergency where relevant

6.0	PROCEDURE

The following potential incidents have been identified at the facility: 


· Subsidence
· Minor / Major Fire
· Surface Fire (Operational Area)
· Plant / Vehicle Accident
· Vehicle Collision With Storage Tank
· Explosion 
· Exposure to Unknown Substances
· Major injury
· Bomb Threats
· Protests / Direct Action
· External Incidents that Effect Site
· Pandemics/Epidemics
· Total Site Evacuation
· Spillage and Leakage
· Adverse Weather Conditions

The procedures for each event identified above are defined in Appendix One. 









7.0	HAZARDOUS MATERIALS (as identified by COSHH assessments)

There are minimal quantities of hazardous materials stored for use on site: 
· Kitchen
· Cleaning Materials

· Offices
· 


· Storage area
· Solvents
· Oil

































	
	
	











APPENDIX ONE

 INCIDENT CONTROLLER PROCEDURES

FLOODING

Risk

Based on a review of the Resources Wales indicative Flood Plain maps, the installation is not located within a flood plain area. It is therefore considered that the likelihood of the installation flooding is low

Notwithstanding this, if appropriate, perimeter ditches will be installed around the perimeter of the installation to intercept water from surrounding higher land, and divert it away from the installation.

Action Plan

	1
	Appoint Incident Controller (Personnel will follow instructions issued by Incident Controller).
	· 

	2
	Carry out a stop and think assessment (Personnel will not attempt to enter a flooded area until a stop and think assessment has been undertaken or the flood has subsided).
	· 

	3
	Isolate all relevant systems in the area of risk such as:
	

	
	Electrical supplies
	· 

	
	Stocks of chemicals and fuel
	· 

	
	
	

	
	
	· 

	4
	If spillage has occurred refer to “Spillage & Leakage” Procedure
	· 

	5
	Consideration should be given to the segregation of “clean” and “dirty” water. 
	· 

	6
	Consideration should be given to a pumping regime.
	· 

	7
	Following remedial action to clear the floodwater, an approved contractor will check all affected electrical supplies.
	· 

	8
	Inform Natural Resources Wales
	· 




SUBSIDENCE

Risk

The permit does not require existing sites to consider subsidence within the emergency management plan.

Action Plan

	1
	Appoint Incident Controller (Personnel will follow instructions issued by Incident Controller).
	· 

	2
	Carry out a stop and think assessment (Personnel will not attempt to enter the affected area until a stop and think assessment has been undertaken).
	· 

	3
	Isolate the affected area.
	· 

	4
	Contact a suitably qualified engineer.
	· 




FIRES – MINOR/MAJOR FIRE

Risk

Installation buildings contain electrical appliances and other sources of ignition along With materials that readily burn.

Maintenance activities on vehicles and equipment can also represent a potential fire risk.

Controls in place to mitigate the risk are:
Fire alarms (Air horn)
Fire fighting equipment,
No smoking policy,
Permit to work for hot works
Provision of trained Incident Controllers, and
Regular disposal of combustible office waste.

Based on the control measures that exist and the operational history it is considered that there is a low risk of fires at the site. Based on the control measures in place at the site, together With the proposed actions in the unlikely event that a fire occurs, it is considered that the risk of significant environmental consequences associated with fires at the site is low.

Action Plan

	Minor
	1
	Raise the alarm and evacuate and isolate the area of all personnel.
	· 

	
	2
	Identify the type of fire and extinguisher needed (see table below).
	· 

	
	3
	Follow the instructions on the extinguisher and attempt to put out the fire if safe to do so.
	· 

	
	4
	If the fire does not go out retreat and class as a major fire.
	· 



	TYPE OF FIRE
	EXAMPLE
	EXTINGUISHER
	COLOUR OF EXTINGUISHER

	SOLID
	WOOD, PAPER, FURNITURE,GREEN
	WATER
	RED

	LIQUID
	OIL, PETROL, SOLVENTS, CHEMICALS
	FOAM / POWDER
	RED WITH CREAM / RED WITH BLUE

	ELECTRICAL
	COMPUTERS
	CO2
	RED WITH BLACK



NB: Do not attempt to tackle gas fires.
 
	Major
	1
	Take the emergency plan folder and visitors book, located in the Site Office as these may be needed
	· 

	
	2
	Contact the EMERGENCY SERVICES. Give as much information as possible about the circumstances and location.
	· 

	
	3
	Meet at the nominated assembly point and take a roll call.
	· 

	
	4
	The INCIDENT CONTROLLER should arrange for the control of traffic and meeting EMERGENCY SERVICES.
	· 

	
	5
	The INCIDENT CONTROLLER is to decide if complete site evacuation is necessary. Refer to total site evacuation if necessary. This may also take place under the guidance of the senior fire officer.
	· 

	
	6
	Any water used to control the fire should be contained Within the site and disposed of safely.
	· 

	
	7
	At a suitable time site managers and other relevant people on the call out list (as detailed at the beginning of this document), including Natural Resources Wales should be informed of the incident.
	· 

	
	8
	Review and update any relevant RA/SWP procedures
	· 



INCIDENT CONTROLLERS

	Location
	Name

	South Wales
	                  Darren Hemming

	Briton Ferry
	
Michael Adams

	
	

	
	



FIRES – SURFACE FIRE (OPERATIONAL AREA)

Risk
Many waste materials that are delivered to the installation will support combustion. Some loads are liable to be delivered in a “hot” condition.

Controls in place to mitigate the risk are:
Fire fighting equipment,
Waste approval system
Waste inspection
No smoking policy,
Permit to work for hot works, and
Provision of trained Incident Controllers.

Based on the control measures that exist and the operational history it is considered that there is a low risk of fires at the site. Based on the control measures in place at the site, together with the proposed actions in the unlikely event that a fire occurs, it is considered that the risk of significant environmental consequences associated with fires at the site is low.

Action Plan

	1
	Raise the alarm and evacuate the area of all unnecessary personnel and vehicles to the nearest mobile assembly point.
	· 

	2
	A roll call of all visitors, contractors and staff Will be carried out.
	· 

	3
	If the fire appears to have been extinguished this should be monitored for the following 24 hours.
	· 

	4
	If the fire does not go out contact the EMERGENCY SERVICES. Give as much information as possible about the circumstances and location.
	· 

	5
	The INCIDENT CONTROLLER should arrange for the control of traffic and meeting EMERGENCY SERVICES.
	· 

	6
	The INCIDENT CONTROLLER is to decide if complete site evacuation is necessary. Refer to total site evacuation if necessary. This may also take place under the guidance of the senior fire officer.
	· 

	7
	Any water used to control the fire should be contained Within the site and disposed of safely.
	· 

	8
	At a suitable time site managers and other relevant people on the call out list (as detailed at the beginning of this document), including Natural Resources Wales should be informed of the incident.
	· 

	9
	Records of any fires will be kept on a fire report form. Copies of the fire report forms are forwarded to Natural Resources Wales
	· 

	10
	Review and update any appropriate RA/SWP procedures
	· 




FIRE IN OPERATIONAL AREA

Risk

	A fire in the operational area is not uncommon and should be dealt with using site staff and equipment. The Site Manager should be informed immediately and take steps to inform the local fire brigade who will take the decision on whether to attend or not. All tipping operations must be suspended and any vehicles or plant in the vicinity of the fire evacuated, if it is safe to do so. 	

Action Plan

	1
	Raise the alarm and evacuate the area of all unnecessary personnel and vehicles to the nearest mobile assembly point.
	· 

	2
	Suspend all tipping operations.
	· 

	3
	Remove any vehicles in the vicinity of the fire if it is safe to do so
	· 

	4
	If the fire does not go out contact the EMERGENCY SERVICES. Give as much information as possible about the circumstances and location.
	· 

	5
	The INCIDENT CONTROLLER should arrange for the control of traffic and meeting EMERGENCY SERVICES.
	· 

	6
	The INCIDENT CONTROLLER is to decide if complete site evacuation is necessary. Refer to total site evacuation if necessary. This may also take place under the guidance of the senior fire officer.
	· 

	7
	Any water used to control the fire should be contained Within the site and disposed of safely.
	· 

	8
	At a suitable time site managers and other relevant people on the call out list (as detailed at the beginning of this document), including Natural Resources Wales should be informed of the incident.
	· 

	9
	Records of any fires Will be kept on a fire report form. Copies of the fire report forms are forwarded to NRW.
	· 

	10
	Review and update any appropriate RAs/SWPs procedures
	· 



FIRES – OFFICE FIRE

Fire Action Notices are displayed throughout the offices.  You should familiarise yourself with these instructions so that in the event of the alarm sounding you know what to do

	1
	Raise the alarm and evacuate the area of all unnecessary personnel and vehicles to the nearest mobile assembly point located on the grass verge outside the gates
	· 

	2
	Evacuate as soon as the alarm sounds – do not go out of your way to collect personal belongings
	· 

	3
	Follow the evacuation arrows to your nearest safe emergency exit.  Your nearest safe emergency exit will not necessarily be the normal exit route therefore it is important you follow the signage.
	· 

	4
	Incident Controllers will check each area and then report to the Fire Assembly Point 
	· 

	5
	Remain at the Assembly Point until given instruction to do otherwise Do not under any circumstances re-enter the building until given authority to do so.
	· 

	6
	The main Incident controller will check in each incident controller as they arrive at the fire assembly point, noting reports on the whereabouts of people who are known to be left in the building/site and if any signs of fire have been seen during the sweep and evacuation of the building/site.
	· 

	7
	The Incident Controller will direct a Fire Marshall to meet the emergency services on arrival and escort them to the alarm activation point.
	· 

	8
	At the Fire Control Point the Incident Controller will liaise with the Senior Crew Member from the emergency services who will assume responsibility
	· 

	9
	When emergency services are satisfied that no danger exists they will instruct the Incident Controller.
	· 

	10
	Once emergency services have departed the Incident Controller will give the instruction to re-enter the building. 
	· 

	11
	The Incident Controller will remain at the Fire Control Point until all staff have re-entered the building and will liaise with Fire Marshals to evaluate the evacuation procedure.
	· 

	12
	At a suitable time site managers and other relevant people on the call out list (as detailed at the beginning of this document), including Natural Resources Wales should be informed of the incident.
	· 

	13
	Review and update any appropriate RA/SWP procedures
	· 





Visually Impaired

	1
	Blind/visually impaired persons will be advised and an Incident Controller will initially walk the person through the evacuation and to the assembly points on arrival to the facility


	· 

	2
	Information will also be given to the Incident Controller for the area that the person will be located so that in the event of an evacuation assistance can be given.




	· 



Hearing Impaired

	1
	There are no visual fire signals within the office/site. Hearing impaired persons who are likely to be working in an isolated area are to advise an Incident Controller for that area and their immediate supervisor so that they may be notified of any alarm.
	· 



Evacuation of Children 

On arrival the site will appoint for the visit a nominated Incident Controller 

A copy of the evacuation procedure and location of escape routes and fire assembly point will be supplied to the schools nominated person(s). 

	1
	On hearing the alarm a continuous tone you will evacuate the building/site through the nearest available exit
	· 

	2
	When evacuating the building/site act calmly and quietly to avoid alarming / scaring the children
	· 

	4
	If children have arrived by coach escort them onto the coach and take the register.
	· 

	5
	Report any missing children to your appointed Incident Controller do not return to the building in the event of reported missing children.
	· 

	6
	Ask other children as to there last known location, report to Incident Controller any information.
	· 

	7
	The incident controller will report children missing and details to the emergency services
	· 



In the event of NO INDICATION OF FIRE i.e. FALSE ALARM

A dynamic assessment is carried out and the Incident Controller in charge may only instruct an Incident Controller accompanied by another to re-enter the building if there is;

NO INDICATION OF FIRE.

	1
	The Incident Controller in charge verifies that no reported signs of fire have been made
	· 

	
	
	· 

	2

	An Incident Controller and another (not the Incident Controller in charge) enter the building/area carrying a fire extinguisher and proceed to visually check for signs.

	· 

	3
	Any indication of fire, such as smell or sight of smoke or flames, must be taken as the signal to leave the building/area immediately and to notify the Incident Controller in charge requesting the attendance of the Fire and Rescue Service.
	· 

	
	
	· 

	4
	The Incident Controller and another leave the building and report their findings back to Fire Control Point

	· 

	5
	The Incident Controller will then if need be, summon the emergency services dialling 999.  
	· 

	6
	Give the operator your telephone number and ask for "Fire Brigade", when the fire brigade replies give the site address and any details known 
Do not assume that the call has been received until it has been acknowledged by the fire brigade.

	· 


PLANT / VEHICLE ACCIDENT

In the event of an accident involving any item of plant or vehicle, the person first becoming aware of the incident must immediately check for casualties.

This includes accidents on the active areas along with any accidents within the site boundary

Any spillage will be dealt with as in the spillage and leakage procedure. 

Action Plan

	1
	Raise the alarm and evacuate the area of all unnecessary personnel and vehicles to the nearest mobile assembly point.
	· 

	2
	Appoint Incident Controller (Personnel will follow instructions issued by Incident Controller).
	· 

	3
	Suspend all tipping operations [if applicable]
	· 

	4
	Check for casualties.
	· 

	5
	If there are any casualties the First Aider must be summoned and the emergency services called. 
	· 

	6
	The INCIDENT CONTROLLER should arrange for the control of traffic and meeting EMERGENCY SERVICES.
	· 

	7
	Check for immediate danger and give first aid.
	· 

	8
	The plant item or vehicle must not be moved, unless to remove casualties, until the Site Manager has assessed the situation and obtained any evidence as to the cause.
	· 

	9
	The accident details should be noted in the site log.
	· 

	10
	The site manager should carry out an investigation in the appropriate forms and initiate any corrective action.
	· 

	11
	In the event of the plant being considered at critical plant, as outlined in the site’s Permit, Natural Resources Wales should be informed
	· 

	12
	In the event that it is an accident involving vehicles on site, contact the insurance company
	· 

	13
	At a suitable time site managers and other relevant people on the call out list (as detailed at the beginning of this document), including Natural Resources Wales should be informed of the incident.
	· 

	14
	Review and update the site traffic management plan, RA and SWP as appropriate
	· 




VEHICLE COLLISION WITH STORAGE TANK


In the event of an accident involving any item of plant or vehicle, with a storage tank the person first becoming aware of the incident must immediately raise the alarm.

Any spillage will be dealt with as in the spillage and leakage procedure. 


Action Plan

	1
	Raise the alarm and evacuate the area of all unnecessary personnel and vehicles to the nearest mobile assembly point.
	· 

	2
	Appoint Incident Controller (Personnel will follow instructions issued by Incident Controller).
	· 

	3
	Check for casualties and follow the first aid procedure if applicable
	· 

	4
	Turn off pumps, if relevant
	· 

	5
	Inform the site manager of the incident
	· 

	6
	The INCIDENT CONTROLLER should arrange for the control of traffic 
	· 

	7
	Manage any spillages / leakages in accordance with that procedure
	· 

	8
	The plant item or vehicle must not be moved, unless to remove casualties, until the Site Manager has assessed the situation and obtained any evidence as to the cause.
	· 

	9
	The accident details should be noted in the site log.
	· 

	10
	At a suitable time site managers and other relevant people on the call out list (as detailed at the beginning of this document), including Natural Resources Wales should be informed of the incident.
	· 

	11
	The site manager should carry out an investigation in the appropriate forms and initiate any corrective action.
	· 

	12
	Review and update the site traffic management plan, RA and SWP as appropriate
	· 





 
EXPLOSION

Risk

The main risk of explosion at the installation is associated with gas bottles 

There is not a history of explosions at the site. Waste assessment and acceptance procedures, waste and product storage and Company health and safety procedures it is considered that the risk of explosions at the site in the future is low.

There is also a potential risk for explosive materials to be delivered to site as part of a waste load.

Action Plan

	1
	Upon discovery of any potentially explosive material the area should be evacuated immediately.
	· 

	2
	Appoint INCIDENT CONTROLLER (Personnel will follow instructions issued by Incident Controller).
	· 

	3
	Carry out a stop and think assessment (Personnel will not attempt to enter the affected area until a stop and think assessment has been undertaken).
	· 

	4
	Contact the EMERGENCY SERVICES and give as much information as possible about the circumstances and location.
	· 

	5
	The INCIDENT CONTROLLER should arrange for the control of traffic and meeting EMERGENCY SERVICES.
	· 

	6
	In the event of an explosion the action taken should be the same as that taken in the event of a fire.
	· 

	7
	At a suitable time site managers and other relevant people on the call out list (as detailed at the beginning of this document), including NRW should be informed of the incident.
	· 

	8
	Review and update any appropriate RA/SWP procedures
	· 




 
EXPOSURE TO UNKNOWN SUBSTANCES

If a material is suspected of being hazardous, evacuate the area and seek assistance from the Emergency Services or NRW

Any spillage will be dealt with as in the spillage and leakage procedure. 

Action Plan

	1
	Avoid contact.  Raise the alarm and evacuate the area of all unnecessary personnel.
	· 

	2
	Appoint Incident Controller (Personnel will follow instructions issued by Incident Controller).
	· 

	3
	Check for casualties.
	· 

	5
	If there are any casualties the First Aider must be summoned and the emergency services called. 
	· 

	6
	Check for immediate danger and give first aid.
	· 

	7
	Stop any carriers leaving site and quarantine any areas as necessary
	· 

	8
	The emergency details should be noted in the site log.
	· 

	9
	At a suitable time site managers and other relevant people on the call out list (as detailed at the beginning of this document), including NRW should be informed of the incident.
	· 

	10
	The site manager should carry out an investigation in the appropriate forms and initiate any corrective action.
	· 

	11
	Review and update any appropriate RA/SWP  procedures
	· 




MAJOR INJURY

Risk

FCC facilities are potentially dangerous places with numerous hazards presenting risks to site personnel, visitors and contractors.

These risks are mitigated by:
Safe operating procedures,
Risk assessments, 
Method Statements,
Permit to Work Procedures, and 
Training

Action Plan

	1
	Immediately request FIRST AID assistance (Refer to the list below).
	· 

	2
	If necessary phone EMERGENCY SERVICES. Give as much information as possible about the injured person and the location.
	· 

	3
	Only approach the injured person if it is safe. Do not move the person unless they are in immediate danger.
	· 

	4
	Keep the injured person warm, and keep talking to them. DO NOT leave them alone.
	· 

	5
	FIRST AIDERS will be competent to deal with the situation until the ambulance arrives.
	· 

	6
	The INCIDENT CONTROLLER is to ensure that traffic is controlled and that EMERGENCY SERVICES are directed to the incident.
	· 

	7
	The site manager should carry out an investigation in the appropriate forms and initiate any corrective action.
	· 

	8
	Notify H&S Manager where necessary
	· 

	9
	Review and update any appropriate RA/SWP procedures
	· 




FIRST AIDERS 

	Location
	Name

	Pwllfawatkin
	Paul Bennett

	
	
                  

	
	
                  



 
BOMB THREATS

Risk

Any threat should be taken a serious.

Action Plan

	1
	Raise the alarm.
	· 

	2
	If not already done the EMERGENCY SERVICES should be contacted and provided with as much information as possible about the circumstances and location.
	· 

	3
	Follow the advise given by the emergency services
	· 

	4
	Evacuate the area and follow the total site evacuation procedure
	· 

	5
	Contact External Affairs 
	· 

	6
	Adhere to the FCC Standard on external communication
	· 



In the event that the site is unable to remain open or is required to close the following should be followed;

	1
	In the event that the facility has to close, drivers and customers will be informed of the decision.
	· 

	2
	Communication will be made with senior management and the appropriate regulatory authority
	· 

	3
	Notification of site closure will be communicated as soon as is reasonably practical
	· 

	4
	Alternative sites will be contacted to determine the availability of other facilities where applicable
	· 

	5
	Where possible alternative arrangements will be communicated and made available to customers
	· 

	6
	Regular contact will be maintained with all parties to keep them abreast of conditions on site and the likelihood of site reopening
	· 

	7
	Communication Will be made to all parties including External Affairs when a decision has been made to reopen the site
	· 



PROTESTS/DIRECT ACTION 
EXTERNAL INCIDENTS THAT EFFECT SITE
PANDEMICS / EPIDEMICS

Risk

Protest and external incidents can result in trespassing on site and security issues for both site and the personnel employed there. Pandemics and epidemics may also result in the possible closure of the site. In the event that this happens refer to the site closure section.

Action Plan

	1
	Inform site manager of potential issue if know prior to organised incident
	· 

	2
	Contact External Affairs for advise
	· 

	3
	Adhere to the FCC Standard on external communication 
	· 

	4
	Review the site security RA to ensure that it is suitable
	· 

	5
	Consider employing additional security if required
	· 



In the event that the site is unable to remain open or is required to close the following should be followed;

	1
	Where conditions are anticipated prior notice will be given to the Sales Department and to customers
	· 

	2
	In the event that the facility has to close, drivers and customers will be informed of the decision.
	· 

	3
	Communication will be made with senior management and the appropriate regulatory authority
	· 

	4
	Notification of site closure will be communicated as soon as is reasonably practical
	· 

	5
	Alternative sites will be contacted to determine the availability of other facilities where applicable
	· 

	6
	Where possible alternative arrangements will be communicated and made available to customers
	· 

	7
	Regular contact will be maintained with all parties to keep them abreast of conditions on site and the likelihood of site reopening
	· 

	8
	Communication will be made to all parties including External Affairs when a decision has been made to reopen the site
	· 



TOTAL SITE EVACUATION

Risk

Any of the enclosed procedures, or an off site emergency, may lead to a total site evacuation.

Action Plan

	1
	Raise the alarm.
	· 

	2
	If not already done the EMERGENCY SERVICES should be contacted and provided with as much information as possible about the circumstances and location.
	· 

	3
	ALL personnel are to be contacted by any means possible and must evacuate the site. If necessary seek alternative routes.
	· 

	4
	Take the emergency plan folder and visitors book, located Site Office, as these may be needed.
	· 

	5
	All personnel are to meet at the assembly point unless it is dangerous and then the incident controller will direct all persons to a safe alternative. Take a roll call.
	· 

	6
	Appoint traffic controller and ensure that all traffic is stopped.
	· 

	7
	Customers should be contacted to prevent more vehicles arriving at site.
	· 

	8
	Operations can only recommence once EMERGENCY SERVICES or INCIDENT CONTROLLER gives the all clear.
	· 

	9
	At a suitable time site managers and other relevant people on the call out list (as detailed at the beginning of this document), including NRW should be informed of the incident.
	· 

	10
	The site manager should carry out an investigation in the appropriate forms and initiate any corrective action.
	· 

	11
	Review and update any appropriate RAs/SWPs procedures
	· 




SPILLAGE & LEAKAGE

Risk

Spillage and leakage can occur during Collection of oils, vehicle breakdowns, accidents and/or damage to tanks and bunds.

The potential risks are mitigated by:
Controlled unloading using trained personnel of all potentially polluting materials,
Appropriate storage vessels (either double skinned or bunded to 110%),
Regular inspection of storage vessels, and
Maintenance of a spillage/leakage kit including absorbent and containment equipment.

Action Plan

	1
	Appoint Incident Controller (Personnel will follow instructions issued by Incident Controller).
	· 

	2
	Carry out a stop and think assessment (Personnel will not attempt to enter the affected area until the nature of the spillage has been ascertained and what harmful effects it could have to human health and safety).
	· 

	3
	If practical ensure that the area is coned off with cones placed at a suitable distance from the spillage.
	· 

	4
	If possible the leak should be stopped and the cause of the leak isolated, and/or moved to a bunded area (e.g.; leaking vehicle or tank).
	· 

	5
	If the spillage can leave site via ditches or drains, the first action must be to stop it. This can be achieved by damming with spoil/clay or by the use of control valves at discharge point.
	· 

	

	6
	Once the spillage has been isolated the various remedial methods listed below should be reviewed and the best option employed.
	· 

	7
	The site manager should be contacted at the first available point.
	· 

	8
	Any spillage outside of the operational area must be reported to the site manager and the environmental technician (if applicable)
	· 

	19
	Natural Resources Wales should be contacted regarding any spillage that threatens to leave site causing pollution.
	· 

	10
	All spillages must be recorded in the environmental log.
	· 

	11
	The site manager should carry out an investigation in the appropriate forms and initiate any corrective action.
	· 

	12
	Review and update any appropriate RAs/SWPs, and procedures
	· 
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Various remedial methods are available:

· Dilution: If the spill is relatively small it may be possible to dilute the liquid with large quantities of water. The water should not be allowed to leave site.
· Soak up booms/Mats: These may be used to soak up the spill and block off exit routes.
· Spillsorb: This may be used to soak up the spill.

NB. All materials used must be disposed of properly and if necessary sent off site.

Pollutants:

Risk

The main potential pollutants at Pwllfawatkin HWRC are Waste Oils


Oils

Is oil based and has a specific gravity of that less than water. This causes oil to float on the surface of the watercourse. If handled correctly oil can successfully be extracted from the water.

	1
	Locate the source of pollution
	· 

	2
	Stop and contain the source of contamination e.g. Insert runoff ditch sluice boards, placement of catchment bunds.
	· 

	3
	Deploy containment measures.
	· 

	4
	Remove and dispose of any contained diesel to avoid any further contamination.
	· 



ADVERSE WEATHER CONDITIONS


In the event of adverse weather the following procedure will be adhered to:



	1
	A decision on whether to close the site in adverse weather conditions will be co-ordinated by the Site Manager or Site Supervisor
	· 

	2
	Weather reports will be monitored daily and in the event of adverse conditions this frequency will be increased
	· 

	3
	Wind speeds will be assessed and monitored at regular intervals dependant on conditions.
	· 

	4
	Primary consideration will be placed on the safety of drivers in relation to opening trailer doors and to banksman and drivers in relation to windblown debris
	· 

	5
	The assessment will take in to consideration wind direction, wind speed and gust speed.
	· 

	6
	Where adverse weather conditions are anticipated prior notice will be given to the Local Authority and to customers
	· 

	7
	In the event that the facility has to close due to adverse weather conditions the drivers and customers will be informed of the decision.
	· 

	8
	Communication will be made with senior management and the appropriate regulatory authority
	· 

	9
	Notification of site closure will be communicated as soon as is reasonably practical
	· 

	10
	Alternative sites will be contacted to determine the availability of tipping facilities where applicable
	· 

	11
	Where possible alternative tipping arrangements will be communicated and made available to customers
	· 

	12
	Regular contact will be maintained with all parties to keep them abreast of conditions on site and the likelihood of site reopening
	· 

	13
	Communication will be made to all parties when a decision has been made to reopen the site
	· 

	14
	Remedial and preventative environmental actions will follow the site’s environmental aspect RA and any Permit requirements

	· 
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APPENDIX ONE

 INCIDENT CONTROLLER PROCEDURES





 
	







Drawing 1. Location of sensitive receptors and prevailing wind direction.

	No
	Receptor
	Category
	Distance
M
	Direction
	Prevailing
wind

	1
	Houses
	Residential
	1000
	E
	Low


	2
	landfill
	Buisness
	50
	N
	High

	3
	A473
	Road
	1000
	E
	Low
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Drawing 2. Site plan 














Drawing 3. Site Drainage Plan
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