INTERNAL USE ONLY

Checklist to be used when assessing Fire prevention and mitigation plans.

Please note:

this checklist has been produced to help you identify and record if the Fire Prevention and Mitigation Plan (FPMP) includes all the relevant information, in accordance with the guidance. This checklist is not a tick box exercise to enable you to determine if the plan is the suitable and each plan must be assessed and considered in terms of the risk of fire and how it will be prevented.

If you are unsure whether the proposed measures are suitable, please check with your Senior Environment/ Permitting Officer.  In addition to this some useful information has been collated on the 01. FPMP query database saved here.

(Produced in accordance with guidance Version 2, August 2017)

Application number: Applicant: Facility Address: Date of assessment: Assessment carried out by: Save a copy in the site folder on the DMS

If the applicant doesn’t follow the minimum standards in the guidance, they must be able to justify why.  The measures they take instead must be equivalent or better.  They must include detailed assessments to satisfy us that the:

- likelihood of fire

- impact from emissions during or after a fire on local people, critical infrastructure and the environment

- resources required by the Natural Resources Wales and other emergency responders during an incident

- post incident clean-up and remediation costs

are equivalent or less than would be incurred if the site followed the minimum standards in this regulatory guidance.

Drafting notes to help complete this assessment record are included and are shown in red. These can be deleted as you work through your assessment.

After you have completed your assessment, if you need to ask the operator/ applicant to submit a revised plan, you can use the same checklist to assess the revised plan. For audit purposes, it makes it easier to read the assessment If you include the “date of the plan” and use a different colored font for different plan versions.

FPMP Checklist summary

| Section | Compliant with guidance? Y / n / N/A | Date of plan / revised plan | Comments |
| --- | --- | --- | --- |
| FPMP Summary | y |  |  |
| Site Plan | y |  |  |
| Common Causes of Fires and Preventative Measures | y | 26th September 2018 | Preventing Fires FPMP p 6, some relevant points missing: - Visitors & Contractors - Reactions between wastes - Hot loads deposited at the site – use a suitable quarantine area for hot loads - Batteries within waste deposits – - Batteries in ELVs |
| Storage Times and self-combustion factors | y |  | Spontaneous combustion and storage FPMP pp 2, 8 |
| Managing Waste Material Stacks and Separation Distances | y |  | In line with the guidance |
| Baled Waste Storage | y | 17th August 2018 | FPMP v.2 – storage times under 3 months |
| Enclosing Stacks Using Bays and Walls | y | 26th September 2018 | The wastes within the bays will not exceed a maximum of 5m x 5m x 5m and will not be stored for periods longer than 8 weeks. FPMP v.4 p.3 |
| Waste Stored Within a Building | n/a |  |  |
| Waste Stored in Containers | y | 01st November 2018 | FPMP v.4 p.3 |
| Layout of Waste Stacks on your Site | y | 17th August 2018 |  |
| Seasonality and Waste Stack Management | n/a | 01st November 2018 | All waste would be stored for up to 3 months – but this still needs to be confirmed |
| Monitoring and Turning of Stacks | n/a |  | Waste will be stored for less than 3 months |
| Fire Detection and Fire Suppression Systems | y |  | Security & Fire Detection/Suppression FPMP v.4 p.8 |
| Firefighting Strategy | y |  | Site Process –in the event of a major fire incident FPMP.v4 P.5 |
| Water Supplies | y |  | The hydrant is available however not ensured the permission. establish water access, available water pressures to your site to ensure that water supplies are available without impacting on local supply. |
| Managing Water Run-off | y |  | Controlling fire water will be a priority during a major incident. Tankers will be used to pump any significant pooling/flooding waters away to protect any environmental receptors locally. The FRS will determine that if the re-use of firewater is appropriate on site. The outlet to the drainage channel will also be sealed using a dam mat to prevent any flow of fire water getting into the ground via the drainage system. |
| Designated Quarantine Area | y | 26th September 2018 |  |
| During and After an Incident | y | 26th September 2018 | Site Process –in the event of a major fire incident FPMP p4 |
| Reviewing and Monitoring your Fire Prevention & Mitigation Plan | y | 26th September 2018 |  |

FPMP Summary

| Does the fire prevention plan specify the following? (the guidance states that it must) | Yes/ No | Comments |
| --- | --- | --- |
| A site plan | y |  |
| the amount and type of waste received daily and how it is managed | Y |  |
| the total amount of waste and the types and forms (e.g. unprocessed, shredded, chipped, fines or baled) that are stored on site at any one time | y | p. 3 v.4 FPMP |
| how each type of waste will be stored | y | p. 3 v.4 FPMP |
| the maximum time each type of waste will be stored on site and how it will be managed | Y | p. 3 v.4 FPMP |
| the location within the site where each type of waste will be stored | y |  |
| the maximum size of any waste pile (in m3), stipulating the maximum length, width and depth | y |  |
| the minimum separation (fire break) distance between waste piles or storage areas | y | Waste storage area p. 7 v.4 FPMP |
| A clear area must be established around the perimeter of site; this can vary depending on the layout of your site and permitted stack sizes in accordance with the separation distances as illustrated in Table 2 (this must be available at all times and identified on your site plan | y |  |
| the fire prevention techniques used, including management of hotspots (sign of potential self-combustion), monitoring, reporting, recording and actions | y | Preventing Fires p. 9 |
| techniques used to minimise the risk of fire spreading within the site or from the site | y |  |
| the steps and procedures to be followed if a fire occurs on your site | y | Site Process –in the event of a major fire incident p.4 of FPMP |
| all combustion products and emissions (to air, land and water) from the fire and the emergency response (including the impact on people, critical infrastructure and the environment) and how they will be minimised. Operator needs to recognise the pollution impact of smoke and fire water and impact on environment and people. |  | Site Process –in the event of a major fire incident p.4 |
| Contact details of sensitive receptors within 1km of your site. To protect sensitive receptors, does the plan include measures that will be used to raise the alarm and to inform local residents, e.g. local school, nursing home etc. These measures will be site specific. Operator may need to check emergency planning procedures with Local Authority. | y | Third version submitted 26th September 2018 |
| how safe access to the site for fire and rescue services and other emergency responders is achieved | y |  |

Site Plan

(could consist of location plan, site plan and drainage plans on one or more plan)

| Does the site plan include the following: The FPMP must include a site plan(s) drawn to scale showing: | Yes/ No | Comments |
| --- | --- | --- |
| layout of buildings | y | Amended site plan dated 26/09/18 |
| any areas where hazardous materials are stored on site (location of gas cylinders, process areas, chemicals, piles of combustible materials, oil and fuel tanks) | y | Site plan |
| main access routes for fire engines and any alternative access | y |  |
| access points around the site perimeter to assist firefighting – see table in guidance for typical FRS vehicle access requirements | y |  |
| hydrants and water supplies | y | Appendix D dated 26/09/2018 |
| any watercourse, borehole or well located within or near the site | n/a |  |
| areas of natural and unmade ground | n/a |  |
| the location of plant, protective clothing and pollution control equipment and materials | y |  |
| drainage systems, foul and surface water drains, and their direction of flow and outfall points | y |  |
| the location of drain covers and any pollution control features such as drain closure valves and firewater containment systems | y |  |
| location of “off- site” emergency information pack with site plan (as specified above) | y |  |
| location of key receptors such as critical infrastructure, schools, hospitals, residential areas, workplaces, protected habitats and rivers within 1km of the site | y |  |
| Location of the quarantine area | y |  |
| compass rose showing north and the prevailing wind direction | y |  |
| Has the applicant included actions to be taken should a fire occur such as: | Yes/ No | Comments |
| reducing the amount of firewater run-off generated - use sprays and fogs rather than jets | y | P. 5 |
| recycling firewater if it’s not hazardous and it’s possible to reuse | y |  |
| applying water to cool unburned material and other hazards, taking care to prevent this water causing or adding to water pollution and/or increasing air pollution | y |  |
| separating unburned material from the fire using heavy plant | y |  |
| separating burning material from the fire to quench it with hoses or in pools or tanks of water (this will reduce the amount of firewater produced) | Y |  |
| using soil, sand, crushed brick and/or gravel (if smoke is threatening local communities) to help suppress the fire, although you can only do this when: |  |  |
| - groundwater vulnerability is low |  |  |
| - agreed as a part of a firefighting strategy by the FRS and supported by NRW |  |  |
| - contaminated material is removed and legally disposed of as soon as it is safe to do so |  |  |
| To decide which of these options, or combinations of options, is appropriate the applicant must consider the following. Have they considered these? | Yes/ No | Comments |
| scale and nature of the environmental hazards on site and the activities that take place on it | y | The operator states in the FPMP that the risks associated with fire are relatively small due to the fact the the waste stored is in small quantities and the turn around of the stored waste would never exceed 3 months at any time. |
| risks posed to people, the environment and property | y |  |
| type of materials you store on site, the form they’re stored in and the length of time needed to extinguish a fire involving them | y |  |
| availability of firewater containment facilities | y |  |
| local topography, weather conditions and fire scenarios that could reasonably be expected on site | y |  |

Common causes of fires and preventative measures

| The FPMP should consider where applicable the common causes of fire, some won’t apply, others need to be included | Yes/ No | Comments |
| --- | --- | --- |
| arson or vandalism | y |  |
| Visitors & contractors | y |  |
| Ignition sources | y |  |
| self-combustion (e.g. due to chemical oxidation) | y |  |
| plant or equipment failure | y |  |
| discarded smoking materials | y |  |
| hot works (e.g. welding or cutting) | n |  |
| industrial heaters | n |  |
| Plant & hot exhausts | y |  |
| damaged or exposed electrical cables | n |  |
| Reaction between wastes | y |  |
| hot loads deposited at the site | N |  |
| Build up loose combustible waste, dust and fluff | N |  |
| “Tramp” metal | y |  |
| Batteries within waste deposits | y |  |
| Batteries in ELVs | y |  |
| Cylinders stored at site | n |  |
| Leaks and spillages of oils and fuels | y |  |

Storage times and self-combustion factors

| Self-combusting materials | Yes/ No | Comments |
| --- | --- | --- |
| Is the applicant storing materials at risk of self-combustion (see list in guidance)? | y |  |
| If yes, are they storing these in line with Table 1 – maximum storage times? | y |  |
| If the applicant is storing materials at risk of self-combustion for longer than 3 months, has the applicant demonstrated additional measures they will take, including monitoring? Guidance states they MUST | n/a |  |
| Has the applicant considered adopting the following fire prevention principles? (Guidance states applicant should consider) |  |  |
| reduce risk factors (e.g. exposed metal content, proportion of 'fines', mixing of materials and heat generated during treatment) |  |  |
| minimise stacks sizes (small stacks with appropriate separation are safer than one larger one) | y | In line with the guidance p.3 of FPMP v.4 |
| control moisture levels | Y | The storage times are not longer than 3 months |
| demonstrate good stock rotation for all stored materials and show how this is monitored and implemented daily | Y | The storage times are not longer than 3 months – |
| store material in its largest form prior to processing e.g. do not undertake preparatory treatments such as size reduction of green waste unless you are intending on submitting the waste to the treatment process immediately | n/a |  |
| monitor and control sub-surface temperature and moisture content with a suitable thermal device (thermal probe/thermal camera) and ensure that this is capable of reaching all parts of a stack (if materials are stored in plastic wrapping you must demonstrate a sampling and testing protocol to ensure a representative number of bales (minimum 10%) are assessed during monitoring | n/a |  |
| routinely turn stacks | n/a | The storage times are not longer than 3 months |
| detect and control hotspots within stacks (Note: steam is a good indicator of self-heating) | y |  |
| define the maximum storage time of all materials on site and show how this will be monitored and controlled | Y |  |
| minimise external heating during hot weather by shading from direct sunlight | y |  |

Managing Waste Material Stacks and Separation Distances

| Guidance says MUST be used | Yes/No | Comments |
| --- | --- | --- |
| Are stack lengths and separation distances in line with Graph 1 for general wastes such as RDF, SRF (Refuse derived fuel/solid recovered fuel - various types of fuel derived from wastes using various treatment processes), wood, paper etc. | y |  |
| Are stack lengths and separation distances in line with Graph 2 for plastics and rubber wastes? | n/a |  |
| Graphs 1 and 2 assume a stack height of 4m, if stack sizes are significantly lower bespoke separation distances can be used – does this apply? | n/a |  |
| Has a competent fire engineer been used to calculate any bespoke separation distances? | n/a |  |
| Storage of whole end of life vehicles (ELVs) Applicant MUST set out in the FPMP how they will store ELVs |  |  |
| Is each vehicle accessible from at least one side allow a fire to be fought and so unburnt vehicles can be accessed and moved to prevent the fire spreading (These rules will limit any row to a depth of 2 vehicles.) | y |  |
| If the applicant proposes to store vehicles one on top of another, or on racking, they should limit this to 3 vehicles high so the stack can remain stable during a fire. You should maintain a minimum separation distance between rows or blocks of vehicles in accordance with Table 2 (depending on the length of the rows) | y |  |
| As part of the applicants’ waste stack management protocol they should consider adopting the following general fire prevention and mitigation principles: | Yes/No |  |
| manage all stacks to within the maximum sizes and minimum separation distances | y |  |
| have availability to adequate water supplies or alternative firefighting methods at all times to fight a fire | y | Additional water supplies provided and confirmend by FRS as suitable |
| enable easy access for emergency vehicles around the whole site | y |  |
| manage all stacks of materials that can self-combust and demonstrate suitable additional precautions if they are stored for more than 3 months | n/a | Non of the waste is to be stored for over 3 months |

Baled waste storage

| The guidance states the FPMP MUST show how they are reducing the risk of fire occurring in bales. | Yes/ No | Comments |
| --- | --- | --- |
| Does the applicant show how they are reducing the risk of fire occurring in bales? | y |  |
| In regards to baled waste storage, it is RECOMMENDED the FPMP show: |  |  |
| what sampling and testing protocol you will use to make sure you assess a representative number of bales (minimum 10%) during monitoring | n/a | Storage time and sizes are in line with the guidance there is no need for special testing |
| that you get representative temperature readings from the centre of the bales; and from bales within the centre of each stack pile | n/a |  |
| that you turn the bales to make sure the waste stays cold | n/a |  |
| If baled waste may exceed limits in Table 1, have additional measures, such as breaking and rewrapping bales been taken? Have additional fire risks that may be introduced from such measures been addressed e.g. sudden introduction of oxygen | n/a |  |
| What is the storage configuration of the bales? Has any fire risk from the configuration been addressed? | n/a |  |

Enclosing stacks using bays and walls

| Guidance states the bays and/or stacks SHOULD be able to provide the following | Yes/ No | Comments |
| --- | --- | --- |
| 120 minutes’ fire resistance period | y | p. 4, v.4 of FPMP |
| The guidance states that the FPMP SHOULD demonstrate: |  |  |
| full and frequent stock rotation and how this will be monitored and recorded | N |  |
| protection from wind | n | . |
| how you intend to check temperature and moisture content of all the material within the bay so that the entire volume of the pile receives representative checks | n/a |  |
| t the construction of the walls in terms of how they offer a thermal barrier and enable cooling | y | Walls of the bays |
| how stock capacity will be managed and controlled | y |  |
| how you will ensure segregation of materials | y |  |
| how calculation of flame height and radiation has been taken into account in preventing the spread of fire between piles | y |  |
| prevention of brands or lighted material moving outside the bay walls | y | A 1 m separation between the bay wall and the waste will be maintained |
| prevention of bridging across or around walls | y |  |
| how a ‘freeboard’ space at the top and sides of the walls will be physically retained at all times in accordance with the latest available guidance | n/a |  |
| the frequency and method of turning piles | n/a |  |
| how the quarantine area will be used and how materials will be moved during an incident | y |  |

Waste stored within a building

| If the applicant is storing waste in a building, the guidance states they SHOULD adopt the following principles at all times | Yes/ No | Comments |
| --- | --- | --- |
| Ensure waste stack sizes and separation distances are appropriate to the risk. Table 2 can be used as a starting point but not absolute guidance for internal storage. General principles should be adopted: | n/a |  |
| Consider the use of fire walls/bunkers. | y |  |
| Separation between internally stored wastes and building walls, plant & other equipment within buildings will need to be considered. In general fires in internally stored wastes are far more likely to spread to buildings and plant than for externally stored wastes. As a result, your insurer is likely to place more emphasis on internal storage than external storage fire management. You should seek advice from your insurer to ensure that you have met any requirements for fire detection and fire suppression. | n/a |  |
| If you are storing wastes internally in large quantities, such as in warehousing, then you should seek competent advice on the precautions to be taken. These will depend on the type of building used, the types of waste being stored and what fire precautions are already in place. This is a specialised area, and the general standards applied to the warehousing of goods may not be appropriate to the internal storage of wastes. | n/a |  |
| If the building is heated this could affect the potential for self-heating of the waste and should be taken into account when assessing self-heating risks. | n/a |  |
| You must ensure that all escape routes, fire exits, alarm call points and fire extinguishers are kept clear and free from waste at all times | y |  |
| Ensure electrical equipment and heaters are kept free from waste, including dust and packaging materials. | y |  |
| Waste storage areas should be fire compartmented away from office areas. | n/a |  |
| Waste storage areas should have some means of clearing smoke from the building, such as openable skylights or roller shutter doors, to aid fire-fighting. | n/a |  |

Waste Stored in containers

| Has the applicant included the following (guidance states you must): | Yes/ No | Comments |
| --- | --- | --- |
| If you store waste in containers that can hold more than 1,100 litres, each one must be accessible so any fire inside it can be extinguished, for all other containers holding waste, the appropriate stack sizes apply as per Table 2 | y |  |
| Guidance states the applicant SHOULD manage containers as follows: |  |  |
| Shipping containers should be stacked no more than 2 containers high and secured with a lock outside of operational hours. | n/a |  |
| If you have a fire, you should be able to move containers as soon as is reasonably practicable in a safe manner to prevent the fire spreading. You should set out in your FPMP the procedures you will put in place to allow this to happen. | y |  |

Layout of waste stacks on site

| In addition to stack sizes, storage methods/types and appropriate separation distances, has the applicant taken into consideration the following factors? (Guidance says these factors MAY need to be taken into account) | Yes/No | Comments |
| --- | --- | --- |
| Location of potential ignition sources on your site | Y |  |
| Location/s of occupied buildings and high-asset value equipment and plant | y |  |
| Escape and evacuation routes around your site and within buildings must not be compromised by stack layout | y |  |
| Location of flammable and/or hazardous substances kept on site, such as gas cylinder cages, diesel tanks, quarantine areas which may contain non-conforming wastes etc. | y |  |
| Locations of on or off-site fire hydrants, other water supplies and fire-fighting equipment – you do not want to block access to these with your stack layout | y |  |
| Proximity and location/s of any infrastructure which may be affected by a fire, such as overhead power lines, major roads, rail lines etc. | y |  |
| Proximity and location/s of any off-site, third party buildings which may be affected by a fire | y |  |
| Permitted amounts of wastes, and types of waste, allowed on site | y |  |
| Location of a ‘quarantine’ area, as appropriate to site specifics | y |  |
| Operational practicalities such as movements of vehicles & designated routes | y |  |
| Stock rotation requirements, seasonality of supply/off-take etc. | n/a |  |
| The applicant should also consider |  |  |
| the prevailing wind, where fire water will flow and the firefighting strategy that will be used. | y |  |

Seasonality and waste stack management

| Has the applicant included the following (guidance states they SHOULD): | Yes/ No | Comments |
| --- | --- | --- |
| provide a technical assessment that shows you have confidence that your proposal will be viable in foreseeable market conditions – this should prove the suitability of materials, the resilience of the supply chain and end user outlets | y |  |
| If the materials on your site are subject to seasonal variation in demand and/or supply you should demonstrate how you intend to manage these variations. You should be able to demonstrate how you will follow the principle of “first in, first out” so that wastes are stored for no longer periods than indicated in Table 1. | y |  |

Monitoring and turning of stacks

| Has the applicant stated how they will achieve this and included the following? (Guidance states they should) | Yes/ No | Comments |
| --- | --- | --- |
| The staff must be trained to detect and manage hotspots. | y |  |
| Piles are monitored regularly and temperature increases and changes in moisture content are minimised. | n/a |  |
| The equipment they use to detect temperature and moisture content must be capable of operating at any depth throughout the pile. Therefore, if they are proposing to have a stack 4m deep, their probe must be capable of operating the depth of the proposed stack. | n/a |  |
| They must explain what indicators they will use in relation to temperature and moisture content and the escalation of actions in relation to these indicators. | n/a |  |

Fire detection and fire suppression systems

| Has the applicant included the following (guidance states they SHOULD): | Yes/ No | Comments |
| --- | --- | --- |
| When deciding what type of system to install you need to take into account that: - the fire and rescue service may not be able to enter the building during a fire - a suppression system may not extinguish a fire, although it may prevent a fire spreading and then allow the fire to be fought effectively by the fire and rescue service - the water supply to a fire system is reliable and adequate at all times | y |  |
| Has the applicant considered fitting the following? (guidance states that they SHOULD consider) | Yes/ No | Comments |
| automatic detection systems such as: |  |  |
| - smoke and heat detectors including temperature probes | y |  |
| - CCTV visual flame detection systems | y |  |
| - spark, infrared and ultraviolet detection | n |  |
| fire suppression systems such as: |  |  |
| - sprinklers | n |  |
| - manual open deluge system | n |  |
| - deluge/water spray systems | n |  |
| - water monitors/cannons/curtains | n |  |

Firefighting Strategy

| Does the applicant have the following resources? (Guidance does not state whether they must have these or need to consider these) | Yes/No | Comments |
| --- | --- | --- |
| (suitable) heavy mobile plant you have available that can be used to move waste around the site, for example loaders, excavators, material handlers | y |  |
| the use of portable water carriers/bowsers can prove to be an essential mechanism to help extinguish fire effected waste | y |  |
| adequately trained staff available | y |  |
| available water supply | y |  |
| finances available for additional resources | y |  |
| Has the applicant described the firefighting techniques that would be employed using the said resources? (Guidance does not state whether they must have these or need to consider these) | Yes/No | Comments |
| applying water to cool unburned material and other hazards | y |  |
| separating unburned material from the fire using appropriate heavy plant | y |  |
| separating burning material from the fire to quench it with hoses or in pools or tanks of water | y |  |
| suffocating the fire using soil, sand, crushed brick or gravel. However, you can only do this if:  Natural Resources Wales has agreed you can do this in the first instance, and  you remove and dispose of contaminated material as soon as it is safe to do so | n/a |  |

Water supplies

| Have they considered the following? (Guidance states applicant MUST have adequate water supplies) | Yes/ No | Comments |
| --- | --- | --- |
| Has the applicant demonstrate that they will have sufficient water supplies available on their site to manage a worst-case scenario incident | y |  |
| Has the applicant described what form their water supply is in? This could be water in storage tanks or lagoons on site, or access to hydrants or mains water supply for example. | y |  |
| Has the applicant referred to alternative water supplies such as a near-by river, canal, lake, lagoon etc. (in some rare cases wells can be used, but their capacity and recharge characteristics must be adequate)? These can be considered within their plan to supplement tanked or mains supplies however these alternative supplies need to be capable of being accessed promptly. | y |  |

Managing fire water

The containment facilities and pollution equipment they need will depend on the size of the site, the amount of material they store and the firefighting strategy.  The CIRIA document 'Containment systems for the prevention of pollution (C736)' may help you identify the facilities and equipment you need for your site.

| The FPMP MUST set out how they will prevent fire water affecting the following receptors? | Yes/ No | Comments |
| --- | --- | --- |
| The local groundwater and surface water bodies | n/a |  |
| Any well, spring or borehole within 50m used for the supply of water for human consumption, including private water supplies | n/a |  |
| Have they considered the following? (Guidance states applicant SHOULD be able to contain run-off | Yes/ No | Comments |
| Where is run off going to? If it is to sewer, a written agreement must be in the FPMP from the sewerage undertaker | n/a |  |
| How will they contain fire water? Has any secondary or tertiary containment been specified? | y | Site Process –in the event of a major fire incident p.4,5 |
| Are their measures suitable? This will depend on the size of the site, the amount of combustible material stored and the firefighting strategy | y |  |
| Is there an environmental risk to the surrounding area? Groundwater/ watercourses/ habitats etc. | n/a |  |

Designated quarantine area

| Has the applicant included the following (guidance states they SHOULD) | Yes/ No | Comments |
| --- | --- | --- |
| the location of this area and the volume of waste that it can hold | y | Third amendment submitted 26th September 2018 |
| Is the quarantine area within the permitted boundary area of the site (guidance states it should) | y |  |
| Does the quarantine area hold at least 50% of the volume of the largest stack, | y |  |
| Does the quarantine area have a separation distance of at least 6 metres around the quarantined waste (this can be decreased if concrete bunkers/walls will be used) | y |  |

During and after an incident

| The FPMP must have contingency measures in place for dealing with issues during and after a fire (Guidance states they MUST) | Yes/ No | Comments |
| --- | --- | --- |
| diverting incoming wastes to alternative sites during a fire | y | Third amendment submitted 26th September 2018 |
| having a plan for how you will notify those who may be affected by a fire, such as nearby residents and businesses | y |  |
| contractors that might be used to assist with additional plant for firefighting techniques, removal of waste material, containment and removal of excess water run-off | y |  |
| how you will clear and decontaminate the site | y |  |
| the steps you must take before the site can become operational again | y |  |

Reviewing and Monitoring your Fire Prevention & Mitigation Plan

| The guidance states that FPMP SHOULD be treated as a live document | Yes/ No | Comments |
| --- | --- | --- |
| Has the applicant described methods and procedures used to maintain compliance as a separate section within your Fire Prevention and Mitigation Plan? | y | Third amendment submitted 26th September 2018 |
| Have they stated the circumstances that would warrant a review, these could include: - Experiencing a fire incident. Following any fire, it is essential that your FPMP (and overall fire management measures) should be reviewed and improved as required to address any issues/concerns - Additional combustible waste streams accepted on site. - Increase waste volumes accepted. - Development of site infrastructure – new buildings. - Installation of new equipment or plant – baler/loading shovel/sort-line/trommel etc. | y |  |
| Have they described the areas of the FPMP that would need updating because of said circumstances? (see the guidance for examples) | y |  |