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Permit with introductory note
The Environmental Permitting (England & Wales) Regulations 2016

Dŵr Cymru Cyfyngedig

Emergency run to waste discharge at Pontsticill Water Treatment Works
Pontsticill
Merthyr Tydfil
CF48 2UP
Permit number
EPR/CB3194FL



Emergency run to waste discharge at Pontsticill Water Treatment Works
Permit Number EPR/CB3194FL
Introductory note
This introductory note does not form a part of the permit
The main features of the permit are as follows.  
Run to Waste (RTW) discharge of dechlorinated drinking water from the Pontsticill WTW. This specification is as determined on the POF008 (Critical Parameter Board) and the discharge shall be made in accordance with the Pontsticill WTW Emergency Run to Waste Procedure. It is anticipated that this will occur for a maximum of 2hrs at a maximum flow rate of 460l/s (max volume 3300m3) via an 800mm pipe. Flow is the summated flow of the combined outlets of the second stage filters as the forward flow will be isolated removing the inline magflow meter from service and proving to the DWI that there is no forward flow of non-compliant water to public supply.  The site also has a similar discharge activity regulated by permit AN0322601.
The status log of the permit sets out the permitting history, including any changes to the permit reference number.

	Status log of the permit

	Description
	Date
	Comments

	Application PAN-006478
	Duly made 18/10/2019
	Application for discharge of Trade effluent consisting of off-specification dechlorinated drinking water

	Additional information received
	18/10/2019
	Revised ERTW procedure.

	Additional information received
	12/03/2021
	Turbidity and suspended solids monitoring

	Additional information received
	08/04/2021
	Revised ERTW test procedure 26032021

	Permit determined
	10/06/2021
	Permit issued to Dwr Cymru Cyfyngedig




End of introductory note
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The Environmental Permitting (England and Wales) Regulations 2016
Permit number
EPR/CB3194FL
The Natural Resources Body for Wales (“Natural Resources Wales”) hereby authorises, under regulation 13 of the Environmental Permitting (England and Wales) Regulations 2016 
Dŵr Cymru Cyfyngedig (“the operator”),
whose registered office is
Linea  
Fortran Road  
St Mellons  
Cardiff  
CF3 0LT 

company registration number 02366777 
to operate a water discharge activity at
Pontsticill Water Treatment Works
Merthyr Tydfil
CF48 2UP
to the extent authorised by and subject to the conditions of this permit.

Name 									         Date	
	Melissa Broad


	10/06/2021



Authorised on behalf of Natural Resources Wales



Conditions
Management
0. [bookmark: _Ref373938749]General management
[bookmark: _Ref373938830]The operator shall manage and operate the activity:
in accordance with a written management system that identifies and minimises risks of pollution so far as is reasonably practicable, including those risks arising from operations, maintenance, accidents, incidents, non-conformances and those drawn to the attention of the operator as a result of complaints; and
using sufficient competent persons and resources.
Records demonstrating compliance with condition 1.1.1 shall be maintained. 
Any person having duties that are or may be affected by the matters set out in this permit shall have convenient access to a copy of the permit.
Operations
Permitted activities
The only activity authorised by the permit is the activity specified in schedule 1 table S1.1.
The site 
The discharge activity shall take place at the discharge point marked on the site plan at schedule 7 to this permit, and as listed in table S3.2; and, the operating techniques that are the subject of conditions prefixed by 2.3 shall be applied at the location(s) shown, or otherwise described, in schedule 7.
Operating techniques
[bookmark: _Ref373938399]For the activity referenced in schedule 1, table S1.1 the activity shall, subject to the conditions of this permit, be operated using the techniques and in the manner described in the documentation specified in schedule 1, table S1.2, unless otherwise agreed in writing by Natural Resources Wales.
If notified by Natural Resources Wales that the activities are giving rise to pollution, the operator shall submit to Natural Resources Wales for approval within the period specified, a revision of any plan or other documentation (“plan”) specified in schedule 1, table S1.2 which identifies and minimises the risks of pollution relevant to that plan , and shall implement the approved revised plan in place of the original from the date of approval, unless otherwise agreed in writing by Natural Resources Wales.
Pre-operational conditions
The activities shall not be brought into operation until 01/12/2021
Emissions and monitoring
Emissions to water
The limits given in schedule 3 table S3.1 shall not be exceeded.
Emissions of substances not controlled by emission limits
The operator shall take appropriate measures to minimise so far as reasonably practicable the polluting effects of the emissions of substances in the discharge not controlled by emission limits (excluding odour).
Monitoring 
The operator shall, unless otherwise agreed in writing by Natural Resources Wales, undertake the monitoring specified in the following tables in schedule 3 to this permit:
[bookmark: _GoBack]point source emissions specified in tables S3.1 and S3.3.
The operator shall maintain records of all monitoring required by this permit.
An Accessible monitoring point shall be provided and maintained to enable the emissions monitoring programme to be carried out at the monitoring point specified in table S3.3 of schedule 3 and shown marked on the site plan in schedule 7. 
Information
Records
All records required to be made by schedule 3, 4 and 5 to this permit shall:
be legible;
be made as soon as reasonably practicable;
if amended, be amended in such a way that the original and any subsequent amendments remain legible, or are capable of retrieval; and
be retained, unless otherwise agreed in writing by Natural Resources Wales, for at least 6 years from the date when the records were made. 
The operator shall maintain convenient access, in either electronic or hard copy, to the records, plan and management system required to be maintained by this permit. 
Reporting
The operator shall send all reports and notifications required by the permit to Natural Resources Wales using the contact details supplied in writing by Natural Resources Wales.
Within the time period after the end of the reporting period specified in schedule 4 table S4.1 the operator shall, unless otherwise agreed in writing by Natural Resources Wales, submit reports of the monitoring and assessment carried out in accordance with the conditions of this permit, as follows:
in respect of the parameters and monitoring points specified in schedule 4 table S4.1;
[for the reporting periods specified in schedule 4 table S4.1 and] using the forms specified in schedule 4 table S4.2; and
giving the information from such results and assessments as may be required by the forms specified in those tables.
Notifications
Natural Resources Wales shall be notified as soon as reasonably practicable following detection, within the site of the regulated facility of:
any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution; and
any breach of a limit specified in schedule 3 table S3.1.
any other significant adverse environmental effects, which may have been caused by the activity, shall also be notified to Natural Resources Wales as soon as reasonably practicable following detection.
The information provided under condition 4.3.1 shall be supported by sending the information listed in schedule 5 to this permit within the time period specified in that schedule.
Natural Resources Wales shall be notified within 14 days of the occurrence of the following matters, except where such disclosure is prohibited by Stock Exchange rules:
Where the operator is a registered company:
any change in the operator’s trading name, registered name or registered office address; and
any steps taken with a view to the operator going into administration, entering into a company voluntary arrangement or being wound up.
Where the operator is a corporate body other than a registered company:
(a) any change in the operator’s name or address; and
any steps taken with a view to the dissolution of the operator.
Where the operator proposes to make a change in the nature of the activity by increasing the concentration of, or the addition of, or allowing the introduction of, a substance to the activity to an extent that the operator considers could have a significant adverse environmental effect on the receiving waters, and the change is not permitted by emission limits specified within schedule 3 table S3.1 or the subject of an application for approval under the EP Regulations or under the terms of this permit:
Natural Resources Wales shall be notified in writing at least 14 days before the increase or addition or allowing the introduction; and
the notification shall contain a description of the proposed change.
The operator shall notify the Natural Resources Wales, as soon as practicable after receipt of a telemetry warning, that operation of the discharge activity has taken place.
Interpretation
In this permit the expressions listed in schedule 6 shall have the meaning given in that schedule.
In this permit references to reports and notifications mean written reports and notifications, except where reference is made to notification being made “as soon as reasonably practicable”, in which case it may be provided by telephone.


Schedule 1 – Operations 

	Table S1.1 Activities

	Activity reference
	Description of activity
	Limits of specified activity

	A1
	Discharge of trade effluent consisting water treatment works run to waste discharge location
	The rate of discharge shall be controlled to prevent any significant scouring of the bed or bankside of the receiving water



	Table S1.2 Operating techniques

	Activity reference
	Description of documentation
	Parts
	Date Received

	A1
	Pontsticill WTW Emergency Run to Waste test Procedure

	All
	26/03/2021











Schedule 2 – Waste types, raw materials and fuels
Schedule 2 not in use.



Schedule 3 – Emissions and monitoring
	Table S3.1 Point Source emissions to water (other than sewer) – emission limits and monitoring requirements

	Effluent(s) and discharge point(s)
	Parameter  
	Limit (including unit)
	Reference Period
	Limit of effective range
	Monitoring frequency
	Compliance Statistic

	A1 Trade effluent consisting of off- water treatment works run to waste via discharge location
	Maximum daily discharge volume
	4000 m3/day


	Total daily volume
	N/A                                                                
	Whenever a discharge occurs
	 Maximum 

	
	Maximum rate of discharge
	500 litres per second
	Instantaneous (spot sample)
	N/A
	Whenever a discharge occurs
	Maximum

	
	Discharge start and end times
	N/A


	N/A


	N/A


	Whenever a discharge occurs
	N/A



	
	Total available chlorine
	50 µg/l
	Instantaneous (spot sample)
Within first 15 minutes and each hour thereafter
	N/A
	Whenever a discharge occurs
	Maximum
 

	
	pH
	6 to 9
	Instantaneous (spot sample)
	N/A
	Whenever a discharge occurs
	Minimum and maximum

	
	Suspended solids (measured after drying at 105oC)
	25mg/l
	Instantaneous (spot sample)
	Suspended solids sampling is only required when turbidity is greater than 8NTU
	Whenever a discharge occurs
	Maximum
 

	
	Total aluminium as Al
	1000µg/l
	Instantaneous (spot sample)
	N/A
	Whenever a discharge occurs
	Maximum
 



	Table S3.2 Discharge points

	Effluent Name
	Discharge Point
	 Discharge point NGR
	Receiving water/Environment

	A1 Trade effluent consisting of water treatment works run to waste via discharge location
	Discharge location
	SO 05948 11482
	Taff Fechan



	Table S3.3 Monitoring points

	Effluent(s) and discharge point(s)
	Monitoring type
	Monitoring point NGR
	Monitoring point reference

	A1 Trade effluent consisting of water treatment works run to waste via discharge location
	Effluent sampling
	SO 05978 11467
	Monitoring point





Schedule 4 – Reporting
Parameters, for which reports shall be made, in accordance with conditions of this permit, are listed below.
	Table S4.1 Reporting of monitoring data

	Parameter
	Monitoring point reference
	Reporting period
	Period begins

	Duration of total spills, including daily volume, start and end times, instantaneous flow plus reasons for the discharge. Turbidity, Suspended solids (measured after drying at 105oC), Total available chlorine, pH, Total aluminium as Al
	Monitoring point
	Reports to be provided to Natural Resources Wales at the start and end of each discharge and upon request.
	At the start of each discharge event.

	Summary report covering all run to waste activity permits, containing all parameters specified in table S3.1 including turbidity plus including results of investigation into the reasons for the discharge and proposed improvements.
	Monitoring point
	Annually
Report to be submitted within 2 months of the end of the calendar year
	1 January



	Table S4.2 Reporting forms

	Parameter
	Reporting format

	Duration of total spills, including daily volume, start and end times, instantaneous flow plus reasons for the discharge. Turbidity, Suspended solids (measured after drying at 105oC), Total available chlorine, pH, Total aluminium as Al
	Electronic or other format as specified by Natural Resources Wales

	Summary report containing all parameters specified in table S3.1 plus including results of investigation into the reasons for the discharge and proposed improvements.
	Annually - Summary report of compliance with the monitoring programme specified in Table 3.1 in a format specified by Natural Resources Wales






Schedule 5 – Notification 
These pages outline the information that the operator must provide. 
Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.
If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.
Part A
	Permit Number
	EPR/CB3194FL

	Name of operator
	Dwr Cymru Cyfyngedig

	Location of Facility
	Pontsticill Water Treatment Works, Merthyr Tydfil, CF48 2UP

	Time and date of the detection 
	



	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques,  accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 2 hours of detection unless otherwise agreed in writing by Natural Resources Wales 

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released/type or nature of sewage released
	

	Best estimate of the quantity or rate of release of substances and/or duration of discharge
	

	Best estimate of the environmental impact of the discharge
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	



	(b) Notification requirements for the breach of a limit specified in schedule 3 table S3.1 

	The information specified below is to be notified to Natural Resources Wales as soon as reasonably practicable following detection.

	Monitoring point reference/ source
	

	Self monitoring regime (where relevant)
	

	Type of failure 
	Eg maximum and minimum pH and maximum total available chlorine

	Date of sample/event
	

	Parameter
	

	Result and units
	

	Limit and units
	



Part B – to be submitted as soon as reasonably practicable unless otherwise agreed in writing by Natural Resources Wales
	Any more accurate information on the matters for notification under Part A.
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident/breach/exceedance
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	



	Name*
	

	Post
	

	Signature
	

	Date
	


* authorised to sign on behalf of the operator


Schedule 6 – Interpretation 
 “accident” means an accident that may result in pollution.
"annually" means once every year.
“application” means the application for this permit, together with any additional information supplied by the operator as part of the application and any response to a notice served under Schedule 5 to the EP Regulations.
“appropriate measures” for the purposes of the emission of substances not controlled by emission limits condition (condition 3.2.1) do not require the operator to undertake treatment to a level beyond that specified in schedule 1 table S1.1, or to carry out routine monitoring for substances not controlled by emission limits.
“emissions of substances not controlled by emission limits” means emissions of substances to air, water or land from the permitted activities, which are not controlled by an emission limit.
“EP Regulations” means The Environmental Permitting (England and Wales) Regulations SI 2016 No.1154 and words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.
“MCERTS” means Natural Resources Wales’ Monitoring Certification Scheme.
“Natural Resources Wales” means the Natural Resources Body for Wales established by article 3 of the Natural Resources Body for Wales (Establishment) Order 2012. The Natural Resources Body for Wales (Functions) Order 2013 transferred the relevant functions of the Countryside Council for Wales, and functions of the Environment Agency and the Forestry Commission in Wales to the Natural Resources Body for Wales.
"quarter" means a calendar year quarter commencing on 1 January, 1 April, 1 July or 1 October.
“significant pollution” means a high level impact incident as indicated by NRW incident classification system.
“year” means calendar year ending 31 December.


Schedule 7 – Site plan

[image: ]




© Crown Copyright and database right 2021. Ordnance Survey licence number 100019741.
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