# Natural Resources Wales permitting decisions

# Bespoke permit

We have decided to grant the permit for Llyn Gwynant campsite operated by Gwynant Limited.

The application number is PAN-022125

The permit number is EPR/DB3493ZM

This permit regulates an existing discharge of 60m3/day treated sewage effluent from a campsite consisting of 460 pitches, most of which are tent pitches with a maximum of 16 campervans/caravans, discharged to ground to an infiltration system built to British Standard 6297:2007. The discharge is pre-existing and has been in existence since the 1980s when it was served by a septic tank and is currently unregulated. The applicant upgraded to a Sequencing Batch Reactor in 2022, which then passes to vertical reed bed and UV disinfection unit before discharging to an infiltration field. The campsite will be shut from 1st November until 14th March and prior to it re-opening the applicant is proposing to seed in sludge to re-start the treatment system. Alternatively, the treatment plant will be dosed with a synthetic carbon source (i.e. food, e.g. 20% acetic acid solution or similar) for a 3-week period prior to site the opening to establish the activated sludge inventory.

We consider in reaching that decision we have taken into account all relevant considerations and legal requirements and that the permit will ensure that the appropriate level of environmental protection is provided.

Purpose of this document

This decision document:

- explains how the application has been determined

- provides a record of the decision-making process

- shows how all relevant factors have been taken into account

- justifies the specific conditions in the permit other than those in our generic permit template.

Unless the decision document specifies otherwise we have accepted the applicant’s proposals.

Structure of this document

- Annex 1 the decision checklist

# Annex 1: decision checklist

This checklist should be read in conjunction with the Duly Making checklist.

| ### Aspect | ### Justification / Detail | Criteria met |
| --- | --- | --- |
|  |  | Yes |
| Consultation |  |  |  |
| Scope of consultation | The consultation requirements were identified and implemented. The decision was taken in accordance with RGN 6 High Profile Sites, our Public Participation Statement and our Working Together Agreements. | ü |
| ### Responses to web publicising | The application was publicised online from 14 December 2023 to 14 January 2024. No responses were received. | ü |
| Operator |  |  |  |
| Control of the facility | We are satisfied that the applicant (now the operator) is the person who will have control over the operation of the facility after the grant of the permit. The decision was taken in accordance with EPR RGN 1 Understanding the meaning of operator. | ü |
| European Directives |  |  |  |
| Applicable directives | All applicable European directives have been considered in the determination of the application. | ü |
| WFD | WFD stage 2 scoping has been completed and the activity/project is considered as having no risk of causing deterioration or preventing any water body or WFD Protected Area from reaching its objectives and taking account of the advice from technical officers - is considered compliant with the WFD Regulations 2017. |  |
| The site |  |  |  |
| Extent of the site of the facility | The operator has provided a plan which we consider is satisfactory, showing the extent of the site of the facility including discharge points. A plan is included in the permit and the operator is required to carry on the permitted activities within the site boundary. | ü |
| Biodiversity, Heritage, Landscape and Nature Conservation and a designated site under the Wildlife and Countryside Act. | The application is within the relevant distance criteria of a site of heritage, landscape or nature conservation, and/or protected species or habitat. A full assessment of the application and its potential to affect the sites has been carried out as part of the permitting process. We consider that the application will not affect the features of the sites. | ü |
| Habitat Regulation Assessment for a designated site under the EU Habitats Directive | Assessment of Likely Significant Effect: The project has been screened for likelihood of significant effects and, taking account of the advice received from protected sites advisors, is considered not likely to have a significant effect on any Natura 2000/Ramsar site (As documented in section 3.2 of OGN 200 form 1, or section 5 if applicable) | √ |
| Environmental Risk Assessment and operating techniques |  |  |  |
| Environmental risk | We have reviewed the operator's assessment of the environmental risk from the facility. The operator’s risk assessment is satisfactory. The assessment shows that, applying the conservative criteria in our guidance on Environmental Risk Assessment, all emissions may be categorised as environmentally insignificant. | √ |
| Operating techniques | We have reviewed the techniques used by the operator and compared these with the relevant guidance notes. The proposed techniques / emission levels for priorities for control are in line with the benchmark levels contained in the TGN and we consider them to represent appropriate techniques for the facility. Condition 2.3.2 requiring that the infiltration shall be constructed to comply with requirements (a) – (e) has not been included as the infiltration system was installed in 2004. | ü |
| The permit conditions |  |  |  |
| Emission limits | We have decided that emission limits should be set for the parameters listed in the permit: - It is considered that the numeric limits described below at after the reed bed and before the infiltration system will prevent significant deterioration of receiving waters. - Ammoniacal Nitrogen (as N): 20 mg/l - Total Phosphorus as P: 10 mg/l - ATU-BOD as 02: 20 mg/l An additional limit of 0.5 mg/l Ammonia Nitrogen (as N) will be set a monitoring borehole, after the infiltration system. We have imposed numeric limits because either a relevant environmental quality or operational standard requires this. A Phosphorus limit has been set to comply with current planning regulations for developments within SACs. An additional limit of Ammonia at the borehole, after the infiltration system has been added in order to ensure additional protection of the receiving groundwater. | ü |
| Monitoring | We have decided that monitoring should be carried out for the parameters listed in the permit, using the methods and to the frequencies specified. These monitoring requirements have been imposed in order to comply with TGN “How to comply with your Environmental Permit” as this is a large discharge will a maximum daily volume of 60m3/day. The operator will be required to carry out monitoring of Ammonia in accordance with these requirements. We must ensure that the discharge does not exceed the limit of 0.5 mg/l Ammonia in order to protect the receiving groundwater. We made these decisions in accordance with the Environmental Permitting Regulations 2016 and TGN “How to comply with your permit.” | ü |
| Reporting | We have specified reporting in the permit. Reporting frequencies are in line with requirements set out in “How to comply with your Environmental Permit.” We made these decisions in accordance with the Environmental Permitting Regulations 2016 and TGN “How to comply with your Environmental Permit.” | ü |
| Considerations of foul sewer | We agree with the operators justification for not connecting to foul sewer. | ü |
| Operator Competence |  |  |  |
| Environment Management System | There is no known reason to consider that the operator will not have the management systems to enable it to comply with the permit conditions. The decision was taken in accordance with RGN 5 on Operator Competence. | ü |
| Sustainable Management of Natural Resources (SMNR) |  |  |
| Considerations of SMNR - Compliance with our General Purpose | We are satisfied that this decision is compatible with our general purpose of pursuing the sustainable management of natural resources in relation to Wales and applying the principles of sustainable management of natural resources” | ü |
| Environment Wales Act 2016 |  |  |
| Biodiversity and resilience of ecosystems duty | Section 6 of the Environment Wales Act 2016 requires that we seek to maintain and enhance biodiversity in the exercise of our functions, and in so doing promote the resilience of ecosystems, in a manner that is consistent with the proper exercise of our functions. NRW is satisfied that in this case, we have taken into account and had due regard to this duty in so far as it is consistent with the function of determining an application for a groundwater discharge activity permit under EPR2016. | ü |