# New bespoke permit

The application number is:  PAN-025629

The Applicant / Operator is:  Johnsons Hotel Linen Limited

The Facility is located at: MCP gas fired steam boiler at Johnsons Hotel Linen site in Afonwen, Pwllheli, Gwynedd LL53 6NQ

We have decided to grant the permit for the MCP boiler plant serving the Johnsons Hotel Linen site

We consider in reaching that decision we have taken into account all relevant considerations and legal requirements and that the permit will ensure that the appropriate level of environmental protection is provided.

## Purpose of this document

This decision document:

Highlights key issues in the determination

Summarises the decision making process in the decision checklist to show how all relevant factors have been taken into account

Unless the decision document specifies otherwise we have accepted the applicant’s proposals. Read the permitting decisions in conjunction with the environmental permit. The introductory note summarises what the permit covers.

# Key issues of the decision

Our decision includes but is not limited to the following:

Air quality

Owing to the nature and surroundings of the MCP boiler plant, the key issues of the decision related to the potential impact of air emissions on nearby protected habitats sites (SACs, SPAs, Ramsars and SSSI’s – defined below), and the associated Habitats Regulations Appropriate Assessment (HRA) and SSSI asessment.  This will be discussed in this decision document.

## Our decision

This Application is to operate a regulated facility which is subject principally to the Environmental Permitting Regulations 2016 (EPR) and the Medium Combustion Plant Directive (MCPD).  We have decided to grant the permit.

When the application was submitted for a permit for the MCP, in order to make our decision we had to ask the applicant for further information.  The initial application was signed by a person not listed as a director on companies house (relevant person). Written confirmation from a director that the person was authorised to sign on their behalf allowed us to duly make the application on 17/06/24 on behalf of Johnsons Hotel linen limited, and subsequently determined.

The permit contains many conditions taken from our standard Environmental Permit template including the relevant Annexes. We developed these conditions in consultation with industry, having regard to the legal requirements of EPR and other relevant legislation. This document does not therefore include an explanation for these standard conditions. Where they are included in the permit, we have considered the Application and accepted the details are sufficient and satisfactory to make the standard conditions appropriate. This document should be read in conjunction with the application and supporting information and permit.

## The Legal Framework

The permit is granted, under Regulation 13 of the EPR. The Environmental Permitting regime is a legal vehicle which delivers most of the relevant legal requirements for activities falling within its scope. In particular, the regulated facility is:

plant as described by Schedule 25A covering the Medium Combustion Plant Directive (MCPD) regulations

subject to aspects of the Well-Being of Future Generations (Wales) Act 2015 and the Environment (Wales) Act 2016 which also have to be addressed.

Granted a permit after due regard for the Conservation of Habitats and Species Regulations 2017, having screened out using the SCAIL tool for affects on habitats.

Granted a permit after due regard for the Wildlife and Countryside Act 1981 (as amended) and after assessment of possible impact on nearby Sites of Special Scientific Interest (SSSI).

- The permit will regulate 1 Medium combustion plant (MCP), which is a 5.1 MWth industrial boiler, providing heat to Johnsons Hotel Linen facility.  The facility itself does fall under the EPR permitting regime at the time of permitting the MCP.  The boiler is fired on 100% natural gas.

- The MCP is not new, and has been operational on the site since 2016.  Changes to the regulatory framework, as outlined above, mean that this existing MCP >5MWth, was required to have a permit by 2024, and meet specified emission limits by 1st January 2025.

We address the legal requirements directly where relevant in the body of this document. NRW is satisfied that this decision is consistent with its general purpose of pursuing the sustainable management of natural resources (SMNR) in relation to Wales, and applying the principles of SMNR. In particular, NRW acknowledges that it is a principle of sustainable management to take action to prevent significant damage to ecosystems. We consider that, in granting the Permit a high level of protection will be delivered for the environment and human health through the operation of the Facility in accordance with the permit conditions. NRW is satisfied that this decision is compatible with its general purpose of pursuing the sustainable management of natural resources in relation to Wales and applying the principles of sustainable management of natural resources.

Environment Wales Act 2016 – Biodiversity and resilience of ecosystems duty

Section 6 of the Environment Wales Act 2016 requires that we seek to maintain and enhance biodiversity in the exercise of our functions, and in so doing promote the resilience of ecosystems, in a manner that is consistent with the proper exercise of our functions. NRW is satisfied that in this case we have taken into account and had due regard to this duty in so far as it is consistent with the function of determining an application for an EPR permit.

## Air Quality

For this kind of regulated activity, the principal emissions are emissions to air. There are no permit conditions for water, land, energy efficiency odour or noise and Best Available Techniques (BAT) requirements do not apply.

The next sections of this document explain how we have approached the critical issue of assessing the likely impact of air emissions from the facility on human health and the environment and what measures we are requiring to ensure a high level of protection.

We have reviewed the operator's assessment of the environmental risk from the facility. The operator’s risk assessment is satisfactory. The assessment shows that, applying the conservative criteria in our guidance on Environmental Risk Assessment, all emissions may be categorised as either insignificant, or unlikely to cause significant pollution.

### 3.1	Assessment of human health Impact on Air Quality

This section of the decision document deals with the modelling of emissions to air from the stack and its impact on local air quality.  The application showed initial screening of air impacts of the MCP screened out using the SCAIL (simple calculation of atmospheric impact limits) tool, and therefore no further assessment was required (predicted environmental concentration significantly below environmental standard at all human receptors).

### 3.2	Impact on Habitats sites, SSSIs, non-statutory conservation sites

The facility is within the relevant screening distance criteria for protected conservation sites. A full assessment of the application and its potential to affect any of the sites has been carried out as part of the permit determination process.

### 3.2.1 National Site Network/Ramsar sites

The following National Site Network/Ramsar sites are located within the relevant screening distance from the facility (which according to our AQTAG 14 guidance is 1.5 K for plant 5-10 MWth operating on Natural Gas)

- Pen Llyn a`r Sarnau / Lleyn Peninsula and the Sarnau Special Area of Conservation (SAC);

Habitats Regulations Assessment (HRA) is not required because there is no conceivable impact pathway to any National Site Network/Ramsar site. No conceivable impact on any Natura 2000 site, by virtue of the Scail screening tool (insignificant process contributions).

## 3.2.2 SSSI Assessment

The following Sites of Special Scientific Interest (SSSI) are located within 1.5  km of the installation:

- Glanllynnau a Glannau Pen-Ychain i Gricieth Site of Special Scientific Interest (SSSI)

No conceivable impact (insignificant process contributions, as per scail tool)

# Decision checklist

| Aspect considered | Decision |
| --- | --- |
| Receipt of application |  |
| Duly making | The Application was accepted as duly made on 16/05/24. This means we considered it was in the correct form and contained sufficient information for us to begin our determination, but not that it necessarily contained all the information we would need to complete that determination. |
| Confidential application | The Applicant made no claim for commercial confidentiality. |
| Identifying confidential information | We have not identified information provided as part of the application that we consider to be confidential. |
| Requests for information | In order for us to be able to consider the Application duly made, we needed more information. We requested further information relating to who was the operator of the facility Upon receipt of this information we were able to consider the application Duly Made. |
| Operator |  |
| Control of the facility | We are satisfied that the Applicant (now the Operator) is the person who will have control over the operation of the facility after the grant of the permit. We are satisfied that the Applicant will be able to operate the facility so as to comply with the conditions included in the permit. This decision was taken in accordance with current guidance on legal operator for environmental permits. |
| Operator competence |  |
| Relevant convictions | NRW’s COLINS Database has been checked to ensure that all relevant convictions have been declared. No relevant convictions were found. The operator satisfies the criteria in RGN 5 on Operator Competence. |
| Financial provision | There is no known reason to consider that the operator will not be financially able to comply with the permit. The decision was taken in accordance with RGN 5 on Operator Competence. |
| Management system | The Applicant has stated in the Application that they will implement an Environmental Management System (EMS) that will meet the requirements for an EMS in our “How to comply with your environmental permit guidance”. We are satisfied that appropriate management systems and management structures will be in place for this facility, and that sufficient resources are available to the Operator to ensure compliance with all the permit conditions. |
| The facility |  |
| The regulated facility | The regulated facility is subject to EPR because it carries out an activity as described in Schedule 25A of EPR - One existing Medium Combustion Plant aggregated to <50 MWth at a specified location - The Operator has provided the grid reference for the emission points from the plant and the activity is defined in Table S1.1 of the permit. |
| Annex I of MCPD | The information contained within Annex I of MCPD has been provided by the Operator and incorporated into the permit in Schedule 7. |
| The site |  |
| Biodiversity, heritage, landscape and nature conservation | The application is within the relevant distance criteria of a site of nature conservation or habitat. We have assessed the application and its potential to affect all known sites of nature conservation or habitats identified in the screening as part of the permitting process. We have assessed the Operator’s air emissions impact modelling report and consider that emissions will not affect any sites of nature conservation or habitats identified. See Key Issues section above. |
| Environmental risk assessment |  |
| Environmental risk | For this kind of regulated activity, the principal emissions are emissions to air. We have reviewed the Operator’s assessment of the environmental risk from the facility. The Operator’s risk assessment is satisfactory. See Key Issues section above. |
| Operating techniques |  |
| Operating techniques | We have specified the operating techniques and the operator must use the operating techniques specified in Table(s) S1.2A. |
| Permit conditions |  |
| Use of conditions other than those from the template | Based on the information in the application, we consider that we do not need to impose conditions other than those in our permit template. |
| Emission limits | Emission limit value(s) (ELV) have been set for the following substances: Oxides of Nitrogen (200) mg/Nm3 on Natural Gas Normal operation) Emission limit values are defined at a temperature of 273.15 K, a pressure of 101.3 kPa and after correction for the water vapour content of the waste gases and at a standardised O2 content of 15 % for engines and gas turbines, 6 % for solid fuels and 3 % for all other MCPs. The ELV(s) have been set in line with the requirements specified within Schedule 25A of EPR. |
| Monitoring | We have decided that monitoring should be carried out for the parameters listed in the permit, using the methods detailed and to the frequencies specified / should not be carried out. The monitoring requirements have been imposed in order to the Operator to demonstrate compliance with the emission limits specified in the permit, as per the ELV and monitoring frequency requirements specified within Schedule 25A EPR. The Operator will carry out monitoring in accordance with the relevant guidance as specified in the permit These decisions have been made in line with current relevant guidance including TGN M5 and Monitoring stack emissions: low risk MCPs and specified generators - GOV.UK (www.gov.uk) |
| Reporting | We have specified the reporting requirements in Schedule 4 of the permit to ensure data is reported to enable timely review by NRW to ensure compliance with permit conditions. |
| MCPD/SG charges and subsistence fees | The type of application regarding MCPD/SG will have an associated charge. The MCPD/SG application type and number of plant will also form the basis for ongoing subsistence fees. More information on this can be found in our charging scheme on our website. |

National Site Network means the networks of sites in the United Kingdom’s territory consisting of such sites as – (a) immediately before exit day formed part of Natura 2000; or (b) at any time on or after exit day are European sites, European marine sites and European offshore marine sites for the purposes of any of the retained transposing regulations.