## Issue Log
Revision | Date | Originator | Checker | Approver | Description
A | 2024-09-01 |  | A Manns | A Manns
Document reference: | B16383-123532-XX-XX-NN-ZA-DH0126
Information class: | Standard
This document is issued for the party which commissioned it and for specific purposes connected with the above-captioned project only. It should not be relied upon by any other party or used for any other purpose.
We accept no responsibility for the consequences of this document being relied upon by any other party, or being used for any other purpose, or containing any error or omission which is due to an error or omission in data supplied to us by other parties.
This document contains confidential information and proprietary intellectual property. It should not be shown to other parties without consent from us and from the party which commissioned it.

## Queensferry WwTW
| BATc number |  | Issue | Description of the techiques in place and how Operator intends to meet each standard | Supporting Evidence (Reference Documents) | Anticipated Compliance Date |  |  | Shannon's Comments
[6 empty] | Now | 2025 | N/A | Entries shown as compliant by 2023 need to be confirmed on their progress. 2023 to be changed to 2024 - in RFI
For each of the documents currently listed either DWCC need to provide these, or we need to provide a summary of how these BAT are covered by said documents - as currently this isn't evidence- in RFI
OVERALL ENVIRONMENTAL PERFORMANCE
| 1 | Environment Management System (EMS) – ALL of the following:
|  | I. | Management commitment | Dwr Cymru has EN ISO 9001, EN ISO 14001 and EN ISO 55001, this site will be considered for inclusion in ISO 14001 assessment | EN(1) 02 Policy Statement | x
|  | II. | Environmental policy development including CI of performance |  | EN(1) 02 Policy Statement | x
|  | III. | Planning and implementing procedures & targets in conjunction with financial planning & investment |  | SAMP | x |  |  | Expand the meaning and relevance - In RFI
|  | IV. | Implementation of procedures
|  |  | (a) Structure & responsibility |  | IMS(1) 01 Section 24 Roles and Responsibilities. | x
|  |  | (b) Recruitment, training, awareness & competence |  | IMS(1) 01 Section 13 Training, Awareness and Competence | x
|  |  | (c) Communication |  | IMS(1) 01 Section 14 Communication. | x
|  |  | (d) Employee involvement |  | IMS(1) 01 Section 14 Communication. | x
|  |  | (e) Documentation |  | IMS(1) 01 Section 15 Document Control. | x
|  |  | (f) Effective process control |  | IMS(1) 01 Section 15 Document Control. | x
|  |  | (g) Maintenance programmes |  | Planned maintenance is carried out in-line with Planned Maintenance Procedures. External Contractors service and maintain our IMS(1) 01 Section20 Monitoring and Measurement. | x
|  |  | (h) Emergency preparedness & response |  | IMS(1) 01 Section 18 and 19; Emergency Procedures EP(3) 01-22; | x |  |  | Would include the AMP here too
|  |  | (i) Safeguarding compliance with environmental legislation |  | IMS(1) 01 Section 23 and ENF 008 – Environmental Annual Review | x
|  | V. | Checking performance and taking corrective action
|  |  | (a) Monitoring & measurement |  | IMS(1) 01 Section 20 | x
|  |  | (b) Corrective and preventive action |  | IMS(1) 01 Section 21; Corrective Action Procedure SP(2)03 & WO (3) 32 - Level 3 Procedure Permit Notification & Investigation | x
|  |  | (c) Maintenance of records |  | IMS(1) 01 Section 16, DCWW document control procedure (SP(2)04) and DCWW Document Retention Policy (AM_L_PL1_008). | x
|  |  | (d) Independent (where practicable) internal or external EMS auditing |  | IMS(1) 01 Section 17 and Business Systems Audit Procedure SP (2) 05 – Level 2 Procedure | x
|  | VI. | Senior management review of EMS |  | IMS(1) 01 Section 22 Management Review. | x
|  | VII. | Following development of cleaner technologies |  | DCWW constantly looking at cleaner and emerging technologies and innovative methods for sludge treatment. Daily and weekly reports. Comparison of process performance across water sector. |  |  | x | To be justified why not relevant- added as RFI
|  | VIII. | Whole life cycle considerations when designing a new plant i.e. impacts from eventual decommissioning and throughout its operating life |  | SAMP | x |  |  | Expand the meaning and relevance - Added as RFI
|  | IX. | Regular sectoral bench marking |  | DCWW are part of the WaterUK IMS Forum to remain informed and engaged with sectoral changes and expectations. | x
|  | X. | Waste stream management (BAT 2) |  | Biosolids Assurance Scheme (goes to Five Fords for further treatment in the thermal hydrolysis plant before suitable for land spreading) | x |  |  | Add residual Management Plan, DoC documents.
|  | XI. | Inventory of waste water & waste gas streams (BAT 3) |  | Please see BAT 3 for further comment |  | x
|  | XII. | Residues Management Plan – S6.5 |  | Residues for AD activities include digestate and liquors a.k.a. by-products and wastes generated from the treatment of sludge. Residues Management is part of the EMS and is reviewed to ensure compliance with BAT. See Residue Management Plan, ref: B16383-123532-XX-XX-PE-NA-DH0107 - QUY Residue Management Plan October 2024. Resultant Digestate is stored temporarily on site before going to Five Fords for further treatment in the THP. Cake is a useful product as an agricultural fertiliser. Biogas is run through a CHP to generate power to operate and heat the digesters and other site activities. Odours are to be captured and returned to process for treatment, biofilter media will be cleaned and reused where possible. Other residues include grit and screenings and packaging waste (IBC's etc) which are all currently sent to landfill, returned to the supplier or sent for recycling. All residues generate and removed are recorded and reviews for reduction options or minimisation are undertaken on a regular basis. All residues are removed from site using suitably competent waste contractors and sent to appropriately permitted facilities for further treatment or disposal. | x
|  | XIII. | Accident Management Plan – S6.5 |  | AMP developed for the application and includes emergency procedures and DSEAR. See Accident Management plan, ref: B16383-123532-XX-XX-PR-OA-HD0106 - QUY Accident Management Plan October 2024 | x
|  | XIV. | Odour Management Plan (BAT 12) |  | OMP produced as part of the OIA works (ref: B16383-123532-XX-XX-PR-ZA-DH0129 - QUY Odour Management Plan October 2024). OIA ref DCWW221_05_final QUY Odour impact assessment September 2022. | x
|  | XV. | Noise & Vibration Management Plan (BAT 17) |  | A Noise Impact Assessment Technical note has been provided identifying that potential noise from the site will not impact sensitive receptors given the location of plant on the site and the proximity of other noise emitting operations locally (see B16383-123532-XX-XX-NN-ZA-DH0118 QUY Noise and Vibration Management Plan July 2024). This noise impact assessment (NIA ref B16383-123532-XX-XX-AS-ZA-DH0109 - QUY Noise Impact Assessment January 2024) of the operation of the STC demonstrates the calculated rating levels do not exceed background sound levels, indicating low or no impact. | x
| 2 | Improving overall environmental performance – ALL of the following:
|  | a. | Set up and implement waste characterisation & pre-acceptance procedures |  | Biosolids Assurance Scheme (BAS): 1. Source Material Risk Assessment & Controls - UK DCWW are committed to undertaking a full sludge characterisation, where considered necessary. Waste acceptance procedures (ref: B16383-123532-XX-XX-GU-ZA-DH0122 - QUY Waste Acceptance Procedure September 2024). |  | x
|  | b. | Set up and implement waste acceptance procedures |  | BAS: 2. Sludge Treatment; Processes; HACCP & Process Validation Procedures; Biosolids Sampling, Analysis, Parameters & Monitoring - UK. DCWW have a waste acceptance procedure for Domestic Waste Imports (WO(3)19) Waste acceptance procedures (ref: B16383-123532-XX-XX-GU-ZA-DH0122 - QUY Waste Acceptance Procedure September 2024). | x
|  | c. | Set up and implement a waste tracking system & inventory | Our Sludge Logistics govern the feedstocks as part of OfWAT reporting, and have a methodology statement to detail why our monitoring systems are robust, our measurements of feedstocks are detailed and our ISCC accreditation supplements this. | Logger system monitoring and reporting all loads. | x
|  | d. | Set up and implement an output quality management system |  | BAS: 5. Biosolids applications to agricultural land; solid analysis, additions of elements and the Safe Sludge Matrix - UK and Biosolids applications to agricultural land - England and Wales. Biosolids Assurance Scheme (goes to Five Fords for further treatment in the thermal hydrolysis plant before suitable for land spreading) | x
|  | e. | Ensure waste segregation |  | BAS: 1. Source Material Risk Assessment & Controls - UK. No mixing of sludge streams (eg raw and digested) during process. | x
|  | f. | Ensure waste compatibility prior to mixing or blending |  | BAS: 1. Source Material Risk Assessment & Controls - UK and BAS: 2. Sludge Treatment; Processes; HACCP & Process Validation Procedures; Biosolids Sampling, Analysis, Parameters & Monitoring - UK | x
|  | g. | Sort solid incoming waste – S6.4 |  | BAS: 1. Source Material Risk Assessment & Controls - UK and BAS: 2. Sludge Treatment; Processes; HACCP & Process Validation Procedures; Biosolids Sampling, Analysis, Parameters & Monitoring - UK for outputs. No incoming solid waste only liquid sludges. |  |  | x
| 3 | Establish and maintain a waste water and waste gas inventory as part of the EMS - ALL of the following:
Information on characteristics of waste and waste treatment processes
|  | (i)(a) | simplified process flow sheets showing emission sources | For all of BAT 3 below - largely covered by the site’s environmental plans and statutory maintenance’s remit. Our Sludge Logistics govern the feedstocks as part of OfWAT reporting, and have a methodology statement to detail why our monitoring systems are robust, our measurements of feedstocks are detailed and our ISCC accreditation supplements this. We work with our project colleagues to capture this as part of H1 assessments and project scoping to implement the permits in the first place, but we don’t then do anything further to amend the permits or implement additional monitoring. | A general process flow diagram is provided with the permit application (ref: B16383-123532-XX-XX-DR-ZA-DH0115 QUY Block Flow Diagram P02). Other process flows are produced and included in the WOMS. | x
|  | (i)(b) | Process-integrated and waste water/waste gas treatment descriptions including performance |  | Emissions performance documented. | x |  |  | Too vague- Added to RFI
|  | Information on characteristics of waste water streams | [6 empty] | Need to add text here on DWCC propose to implement testing to gain an inventory. The text should match the MSD
|  | (ii)(a) | Mean and variability of:
|  |  | Flow | Waste water stream = return liquors to the head of the wastewater treatment works - this needs to be sampled and analysed in accordance with the | PVSS (m3/day) | x
|  |  | pH |  | DCWW are committed to implementing a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. Flows measured, sampled and analysed for BOD, COD, pH, ammonia and suspended solids. DCWW are committed to undertake sampling and analysis in line with BAT3. |  | x |  | This section needs to be updated as per MSD, once DCWW agree the approach
|  |  | Temperature |  |  |  | x
|  |  | Conductivity |  |  |  | x
|  | (ii)(b) | Mean concentration, load and variability of:
|  |  | Total suspended solids | Centrate and Filtrate sampled daily | ADF 001 | x |  |  | What is ADF? -added to RFI
|  |  | COD/TOC |  | Not currently tested, and therefore the mean and variability is unknown. DCWW are committed to implement a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. DCWW are committed to undertake sampling and analysis in line with BAT3. |  | x
|  |  | Nitrogen species |  |  |  | x
|  |  | Phosphorous |  |  |  | x
|  |  | Metals |  |  |  | x
|  |  | Priority substances/micropollutants |  |  |  | x
|  |  | Any other relevant compounds |  |  |  | x
|  | (ii)(c) | Bioeliminability data (see BAT 52):
|  |  | BOD |  | Not currently tested, and therefore the mean and variability is unknown. DCWW are committed to implement a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. DCWW are committed to undertake sampling and analysis in line with BAT3. |  | x
|  |  | BOD to COD ratio |  |  |  | x
|  |  | Zahn-Wellens test |  |  |  | x
|  |  | Biological inhibition potential |  |  |  | x
Information on characteristics of waste gas streams
|  | (iii)(a) | Mean and variability of:
|  |  | Flow |  | Not currently tested, and therefore the mean and variability is unknown. DCWW are committed to implement a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. DCWW are committed to undertake sampling and analysis in line with BAT3. DCWW confirm that they will characterise emissions from the odour control units in line with BAT 3 to demonstrate if TVOC and HCI are present in the waste gas stream. Where TVOC and HCI are identified as relevant in the waste gas streams then DCWW will continue to monitor these emissions in line with BAT requirements. |  | x
|  |  | temperature |  |  |  | x
|  | (iii)(b) | Mean concentration, load and variability of relevant substances:
|  |  | Organic compounds |  | Not currently tested, and therefore the mean and variability is unknown. DCWW are committed to implement a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. DCWW are committed to undertake sampling and analysis in line with BAT3. DCWW confirm that they will characterise emissions from the odour control units in line with BAT 3 to demonstrate if TVOC and HCI are present in the waste gas stream. Where TVOC and HCI are identified as relevant in the waste gas streams then DCWW will continue to monitor these emissions in line with BAT requirements. |  | x
|  |  | POPs e.g. PCBs |  |  |  | x
Any other relevant compounds
|  | (iii)(c) | Flammability |  |  |  | x
|  |  | Lower and Higher Explosive Limits |  |  |  | x
|  |  | Reactivity |  |  |  | x
|  | (iii)(d) | Presence of other substances that may affect the gas treatment system or plant safety:
|  |  | O2 |  | Recorded 'live' on SCADA | x
|  |  | N2 |  | Not currently tested, and therefore the mean and variability is unknown. DCWW are committed to implement a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. DCWW are committed to undertake sampling and analysis in line with BAT3. |  | x
|  |  | Water vapour |  |  |  | x
|  |  | Dust |  |  |  | x
| 4 | Reducing environmental risk associated with waste storage – ALL of the following:
|  | a. | Optimised storage location | Distance from watercourse? Walls around storage section, drainage all returns to the wastewater treatment works. | Source of waste is indigenous sludge and imported sludge. Solid waste generated as part of the operations is kept inside and kept separately from other wastes. No hazardous wastes accepted. Residue management plan provided in relation to other waste streams. Doc ref B16383-123532-XX-XX-PR-OA-HD0106 - QUY Accident Management Plan October 2024 Storage is in accordance with BAS - 3. Biosolids transportation and storage - England and Wales | x
|  | b. | Adequate storage capacity |  |  | x
|  | c. | Safe storage operation |  |  | x
|  | d. | Separate area for storage & handling of packaged hazardous waste |  |  | x
| 5 | Set up and implement procedures to reduce the environmental risk associated with handling and transfer of waste - include following elements:
|  | Carried out by competent staff |  |  | BAS - 3. Biosolids transportation and storage - England and Wales. See waste acceptance procedure (ref: B16383-123532-XX-XX-GU-ZA-DH0122 - QUY Waste Acceptance Procedure September 2024), DCWW waste acceptance procedure for Domestic Waste Imports (WO(3)19) and Accident Management Plan (ref: B16383-123532-XX-XX-PR-OA-HD0106 - QUY Accident Management Plan October 2024). All DCWW tanker drivers must undergo training as per the driver induction pack (aka Logistics Agency Induction 001). The induction pack consisting of 30 slides must be kept in the cab whilst driving/working at all times and the information enclosed within it must be available available to emergency services. Slide 28 of the induction pack, the provide procedures for the loading from sludge tanker points and discharge to sludge tanker points and are listed as follows: LOADING FROM SLUDGE TANKER POINT 1. Position Tanker so that the hoses can be easily connected from the well point to the lorry and apply the handbrake. 2. Connect hoses from well point to tanker inlet valve, ensuring that the pipes are secure and vent points are closed. 3. Select Suction (Suck) on control panel. 4. Ensure vac/press gauge starts to record a vacuum in the tank. 5. Open valve on sludge tank point if fitted and Inlet valve on Tanker. 6. Observe level on sight glass and close sludge tank point when on full marker as indicated on the sight glass. 7. Open pipe vent at sludge tank point , to allow sludge to vacuum from the hoses. Once drained, close pipe vent, close tanker inlet valve, disconnect hoses and secure outlets with blanking caps. 8. Release vacuum in tank. 9. Close vent valve. DISCHARGE INTO SLUDGE STORAGE TANK 1. Position Tanker so that the hoses can be easily connected from the storage tank to the lorry and apply the handbrake. 2. Connect hoses from Reception tank (Logger if Applicable) to tanker discharge valve, ensuring that the hoses are secure and vent points are closed. 3. Select Pressure (Blow) on control Panel 4. Ensure vac/press gauge starts to record a pressure in the tank. 5. Open valve on sludge tank point via Logger if fitted and Outlet valve on Tanker 6. Observe level on sight glass and once tanker empty, Close Tanker Outlet valve. 7. Turn off tanker pump. 8. Open Tanker Drain Valve to drain and relieve pressure. 9. Disconnect hoses, close Drain valve, secure outlets with blanking caps and hose down any residue or spillages. In addition, the vehicle discharge points are located on an impermeable surface with sealed drainage system. The tankers are DCWW own tankers and only used to transport liquid sludges, therefore, tanker ‘wash-out’ certification is not required. However, tankers are cleaned by the tanker driver drawing off FE from the FE tank. They then drive to the inlet works and discharges the water from the tanker into the inlet works via a pipe. It is not a frequent occurrence. The inlet works has an impermeable surface, wash down (hose) facility and drains to the head of the works to go through the Wwt process. | x
|  | Duly documented, validated and verified |  |  |  | x
|  | Spill prevention, detection and mitigation measures |  |  |  | x
|  | Take precautions when mixing or blending wastes |  |  |  | x
|  | Procedures are risk-based and consider likelihood of accidents, incidents and their environmental impact |  |  |  | x
MONITORING
| 6 | Relevant emissions to water: monitor key process parameters at key locations
Key process parameters
|  | Waste water flow |  |  | NA - any discharge waters are returned back to the head of the waste water treatment works for further treatment under NRW permit consent for wastewater treatment. This site does not currently meet this BAT requirement [As an interim measure DCWW have established a sampling programme based on existing sampling points and substance test list based on our initial understanding. This is currently under review regarding the latest guidance on determinands. We accept this does not currently meet BAT but anticipate it may provide additional useful data to inform future plans. We are developing a wastewater sampling plan and this will be available within [6 months of permit issue]. The plan will be implemented [within 12 months of permit issue[. We plan to meet BAT through implementing the required sampling and testing at appropriate locations on site. Our plans are being developed based on a phased approach to provide data as soon as available. We are revising the substance list to the guidance provided and looking to implement the revised list as soon as possible. At this stage we are not able to understand the full scope required regarding lab facilities to provide BAT compliant testing but plan to test what we can and investigate options for any other requirements. We are limited by the number of existing sampling points and our plans include scopes of work to physically provide the required equipment to complete all required samples and flow measurements. We will undertake further survey and design to determine the technical requirements for a given site and identify a detailed scope of requirements to meet the specifications required. Our initial review has identified some challenges that we are working to resolve, specifically in relation to MCERTS, composite sampling, batched flows and existing pipework geometry. Monitoring locations for each sampling point have been added to the site layout plan. The exact locations remain subject to design development and appropriate documentation will be provided in due course. Development of a sampling plan has commenced and we will be in a position to provide this [within 6 months of permit issue]. |  | x |  | BAT 6 relates to the monitoring of sludge liquors leaving the STC and passing to the head of the works for further treatment in the adjacent WwTW. It is expected that the requirement for the monitoring of sludge liquors returned to the inlet works will be included within the permit initially as an improvement condition to later be imposed as an operational technique. DCWW will need to consider what key parameters to monitor and how, and include training requirements, laboratory fees and implementation into operational instructions and the EMS. - added to RFI
|  | pH |  |  |  |  | x
|  | Temperature |  |  |  |  | x
|  | Conductivity |  |  |  |  | x
|  | BOD |  |  |  |  | x
|  | Other process parameters |  |  |  |  | x
|  | Key monitoring locations |  |  |  |  | x
|  | Pre-treatment inlet and/or outlet |  |  |  |  | x
|  | Final treatment inlet |  |  |  |  | x
|  | Discharge point (to the environment) |  |  |  |  | x
|  | Other location |  |  |  |  | x
| 7 | Monitoring emissions to water (refer to table) |  | No emissions to water | Comply as part of the discharge consent/no direct emissions to water from permit area. NA - any discharge waters are returned back to the head of the waste water treatment works for further treatment under NRW permit consent for wastewater treatment. DCWW are committed to undertake monitoring of waste water, in line with the outcome of the sampling and analysis in line with BAT3. |  |  |  | I Need to check with Anita about this one
Monitoring parameters depend on waste treatment process(es) involved
| 8 | Monitoring emissions to air (refer to table) |  | Covered in EPR Permit | These compliance requirements are already set out in the EPR. Monitoring will be in line with BAT 8 for the following parameters - H2S and NH3 (or odour concentration) and we will follow the relevant EN standard as described under BAT 8 for biological treatment of waste.
Monitoring parameters depend on waste treatment process(es) involved
| 9 | Monitoring diffuse emissions of organic compounds to air from processes involving solvents. Use one or a combination of the following:
|  | a | Measurement – S6.2 descriptions | Not applicable, no burning of solvents |  |  |  | x
|  | b | Emissions factor calculation |  |  |  |  | x
|  | c | Mass balance calculation |  |  |  |  | x
| 10 | Periodically monitor odour emissions where nuisance is expected and/or has been substantiated (monitoring frequency is outlined in BAT 12)
|  | Use EN standards e.g. 13725 or 16841 | [5 empty] | x
|  | Use equivalent methods e.g. ISO / national / international monitoring standards |  |  | See WWWOE (3) 25 - Odour Control Test and the Odour Management Plan [ref: B16383-123532-XX-XX-PR-ZA-DH0129 - QUY Odour Management Plan October 2024] Monitoring will be in line relevant EN and regulator required standard. | x
| 11 | Annual monitoring for:
|  | - Water, energy and raw materials |  | Covered by our annual energy consumption reporting to OFWAT, which requires to report total energy consumption (electricity, gas, heating fuels, transport use) for each regulated area of the business. This data is audited annually by Jacobs before submitting the data to OFWAT. The majority of the energy consumption (all electricity & natural gas use which covers ~90%) is monitored against a budget for each individual facility on a monthly basis. This energy consumption is based on metered data from Automatic Meter Readers and/or invoices from the energy suppliers (Ørsted & Corona). See also Dwr Cymru IMS WO (3) 32 Permit Notification & Investigation. | Energy use onsite measured annually and submitted to NRW as annual return. Covered by our annual energy consumption reporting to OFWAT, which requires to report total energy consumption (electricity, gas, heating fuels, transport use) for each regulated area of the business. This data is audited annually by Jacobs before submitting the data to OFWAT. The majority of the energy consumption (all electricity & natural gas use which covers ~90%) is monitored against a budget for each individual facility on a monthly basis. See also Dwr Cymru IMS WO (3) 32 Permit Notification & Investigation. Other reports are provided to the regulator as required. | x
|  | - Generation of residues and waste water |  | Residues? Wastewater returned to head of works |  | x
EMISSIONS TO AIR
| 12 | Set up, implement and review an Odour Management Plan (as part of the site EMS) where nuisance is expected and/or has been substantiated. Include ALL of the following: | [6 empty] | Should not be listed as N/A. BAT is to have procedures in place to allow a trigger to update the OMP on a routine basis, and when certain number of complaints are received n quick succession or ongoing issue OMP to be checked to confirm triggers for ad hoc reviews to be included
|  | Protocol containing actions and timelines |  | The applicability is restricted to cases where an odour nuisance at sensitive receptors is expected and/or has been substantiated. | See Environmental Impact Control Plan and the Odour Management Plan (ref: B16383-123532-XX-XX-PR-ZA-DH0129 - QUY Odour Management Plan October 2024] |  | x
|  | Protocol for conducting odour monitoring (BAT 10) |  |  |  |  | x
|  | Protocol for response to odour incidents/complaints |  |  |  |  | x
|  | Odour prevention and reduction programme |  |  |  |  | x
| 13 | Techniques to prevent, or where not practicable reduce odour emissions. Use one or a combination of the following:
|  | a. | Minimising residence times (open systems only) |  |  |  |  | x | But In BAT 14 DCWW refer to open storage, need to add the amount of time open systems hold the waste, to prevent odour - added to rRFI
|  | b. | Use chemical treatment (N/A if desired output is hampered) |  | Refer to Odour Impact Assessment doc ref DCWW221_05_final QUY Odour impact assessment September 2022, Odour Management Plan provided as doc ref B16383-123532-XX-XX-PR-ZA-DH0129 - QUY Odour Management Plan October 2024 Environmental Risk Assessment doc ref B16383-123532-XX-XX-AS-ZA-EI0108 - QUY Environmental Risk Assessment October 2024 | x
|  | c. | Optimising aerobic treatment – see examples. Refer to BAT 36 for wastes other than water-based liquid waste. | Preventing foaming of digesters | The aerobic (biological ) treatment stage of the main wastewater treatment process is not part of the STC site. |  |  | x
| 14 | Techniques to prevent, or where not practicable reduce diffuse emissions to air, in particular of dust, organic compounds and odour. Use one or a combination of the following:
|  | a. | Minimising potential diffuse emission sources – see examples | This includes techniques such as: — appropriate design of piping layout (e.g. minimising pipe run length, reducing the number of flanges and valves, using welded fittings and pipes); — favouring the use of gravity transfer rather than using pumps; — limiting the drop height of material; — limiting traffic speed; — using wind barriers. | Existing plant - such design considerations have not been formally recorded. Diffuse emissions from open storage areas are covered in the Odour Management Plan. Pressure Relief Valves (PRVs) are present on digesters, gas bag, and CHP. Pressure release valves (PRV) are present on both primary digesters and the gas holder where there are two on each asset. The digesters and secondary digesters have pressure monitors to monitor gas production rates to prevent excess pressure in storage tanks and vessels. Gas production is monitored by a pressure sensor on these assets which indicates a rise or drop in pressure in an emergency by providing a pre-warning typically at 23mbars and releasing the pressure relief valves typically at 25mbars. PRVs are designed to BS EN ISO 28300:2008 or other recognised standards, if installed earlier, as they would have been installed, and maintained, by a specialist contractor at the time. Use of pressure relief valves is restricted through the use of the CHP engines, and flare if required, at a lower bag volume and pressure. At present, DCWW do not record release events from PRVs as there is no means of recording. When a release has been identified it may be noted in the site diary. SCADA may log a high pressure or a sudden drop in pressure which may indicate the PRV has released. It will not record when the PRV is faulty, although records may be used to identify a report of a PRV fault and action taken. Although long periods of release much be reported to the pollution team and investigation undertaken, but these are more easier to identify by site operatives. |  | x
|  | b. | Select and use high-integrity equipment – see examples | This includes techniques such as: — valves with double packing seals or equally efficient equipment; — high-integrity gaskets (such as spiral wound, ring joints) for critical applications; — pumps/compressors/agitators fitted with mechanical seals instead of packing; — magnetically driven pumps/compressors/agitators; — appropriate service hose access ports, piercing pliers, drill heads, e.g. when degassing WEEE containing VFCs and/or VHCs. | Existing plant - such design considerations have not been formally recorded. |  | x
|  | c. | Corrosion prevention – see examples | This includes techniques such as: — appropriate selection of construction materials; — lining or coating of equipment and painting of pipes with corrosion inhibitors. | All construction and installations are in line with water Industry specifications supplemented with DCWW specifications |  | x |  | Why is this listed as a 2023 goal? What needs to be done? Or was this in error? - add to RFI
|  | d. | Containment, collection and treatment of diffuse emissions – see examples | All processes contained in tanks or buildings, all emissions collected and emitted through the permitted emissions stack. The use of enclosed equipment or buildings may be restricted by safety considerations such as the risk of explosion or oxygen depletion. The use of enclosed equipment or buildings may also be constrained by the volume of waste. | EN (3) 02 - Waste Management Practice provides some general waste practices and the Odour Management Plan provides measures for management of diffuse odour release, but nothing else formally recorded. |  | x
|  | e. | Dampening (with water or fog) |  | Not relevant - no significant potential dust sources on site. |  |  | x
|  | f. | Maintenance – see examples | Access available to all equipment | No specific maintenance procedures in place to cater for this requirement other than annual maintenance schedule with Statutory Maintenance dept. | x
|  | g. | Cleaning of waste treatment and storage areas – see examples | General housekeeping | There are general housekeeping and management tasks undertaken and procedures followed by site operatives on a routine basis including WOF 002 Daily/ AGA 2 task sheets. There are general housekeeping and management tasks undertaken and procedures followed by site operatives on a routine basis however nothing formally documented. Local wash-water hoses are provided to enable prompt clean up, thus minimising any diffuse odour emissions. Some specialist tasks will be carried out based on scheduled inspections i.e. digester internal inspections,. The digesters will be scanned utilising thermal imaging for grit build up, if as a result of the thermal scan it is identified the digester requires a de-grit the de-grit will be completed and at the same time an internal inspection of the digester will be carried out. This is an approach DCWW will be applying to all it’s IED permitted sites and has already been accepted as part of IED permit applications in sites such as Five Fords & Cog Moors WwTW. A leak detection and repair (LDAR) plan will be in place for the Site [ref: B16383-123532-XX-XX-PR-ZA-DH0123 - QUY Leak Detection and Repair Plan October 2024]. | x
|  | h. | Leak Detection And Repair (LDAR) programme for organics – S6.2 |  | Uncontrolled releases of biogas is monitored by pressure instrumentation of the system pressure relief valves, resulting in alarm conditions to warn the site operations team to take corrective action. The Site currently uses SCADA and telemetry monitoring, combined with daily site walkovers with gas monitoring to ensure emissions to air, from leaks are identified and repaired. During routine maintenance a visual walkover surveys for pipework etc is conducted to check for integrity, corrosions and leaks. Leak detection (methane gas analyser) is also installed on biogas holder/s to ensure any leaks from the inner bag are detected. Any leaks detected on the biogas system would always be fixed immediately by DCWW due to the process safety risk of posed by biogas. Site will be checked and inspected through various routes as per all DCWW assets. Site visual inspections will be completed by DCWW at a defined frequency and recorded in our SAP database alongside all other maintenance activities that are carried out on site. The sites also have a robust 24/7 scada system which includes flow and pressure monitoring where required also providing alarms and trending facilities. The scada system is also connected to DCWW central Smart Hub where all alarms are managed out of hours and responded to accordingly, this aligns with DCWW existing processes and procedures. This is an approach DCWW will be applying to all it’s IED permitted sites and has already been accepted as part of IED permit applications in sites such as Five Fords & Cog Moors WwTW.A leak detection and repair (LDAR) plan will be in place for the Site. |  | x
| 15 | Use flaring only for safety reasons or non-routine operating conditions (OTNOC). Use both of the following:
|  | a. | Correct plant design – see examples | Equipment breakdown and excess biogas will result in flaring | Existing plant. Biogas produced by the digestion process is re-used on site in Combined Heat and Power (CHP) engine. The electrical output from the CHP engine is used to power the WTW & STC. Where there is a shortfall compared to the site demand this will be met by importing from the grid, where there is a surplus this will be combusted in the waste gas burner (flare). Used for emergency or non-routine activities and recorded on SCADA/site log for permit compliance. | x
|  | b. | Plant management including gas system balancing and advanced process control |  | There is a gas holder in place to provide storage / balancing of biogas feeding into the CHP. However, when excess gas is generated or when CHP is unavailable, due to downtime or maintenance this will inevitably lead to the operation of the waste biogas burner to allow the treatment process to safely continue effectively and efficiently. DCWW undertook an analysis and the biogas increase did not appear to be great enough as to prompt an increase of the capacity of the engine. CHP engine and boilers to preferentially take biogas. | x |  |  | Can we please get access to this email as Support DoC (could be added to the MSD as an appendix) - added as RFI
| 16 | Reduce emissions to air when flaring is unavoidable. Use both of the following:
|  | a. | Correct design of flaring devices – see examples | Built to specifications at time of Implementation. Flare designed to 150% of biogas. In existing plants, applicability may be restricted, e.g. due to maintenance time availability. | The flare is maintained in accordance with manufacturer's specifications and DCWW’s maintenance requirements. Flare stacks installed to MED 4256. Flare stack location and heights are designed based on modelling relevant to the local area, including prevailing weather conditions. The combustion of the biogas by the flare is as efficient as possible and produces a smokeless emission. The flare is used only during emergencies and when the CHP is on downtime for maintenance Monitoring flare event via flow metre. And report annually as per permit requirements | x
|  | b. | Monitoring and recording as part of flare management – see examples | An H1 assessment has been undertaken. Other H1 assessments have been previously undertaken to document the performance of the waste gas burner and the significance of its emissions when they exceed permit Emissions Limit Values. As a business we have not made funding available to enhance Waste Gas Burner combustion control, from the originally installed specification. We continue to record operating hours and, when greater than 10% of the year, we report as part of our annual permit returns. | Monitoring flare event via flow meter. Report annually as per similar permit requirements for other sites. Flare stack operation is not currently monitored on the Site. Only run times are monitored against a limit of 10%, above which monitoring is then required to ensure the relevant ELV’s are met. Part of Annual reporting when above 10% of time. Quality of gas being flared is not recorded. | x |  |  | Contradictions. One text box states monitoring is undertaken as per permit requirements if over 10% of the year, but then states in the box to the left "Quality of gas being flared is not recorded." - need t be clear if this flare at Queensferry is monitored. - add to RFI
NOISE AND VIBRATIONS
| 17 | Set up, implement, and regularly review a Noise and Vibration Management Plan (as part of the EMS) where nuisance is expected and/or has been substantiated. Include ALL of the following:
|  | I. | Protocol with actions and timelines |  | The applicability is restricted to cases where a noise or vibration nuisance at sensitive receptors is expected and/or has been substantiated. There are currently no protocols in respect of noise and vibration monitoring operating within the business. Noise complaints are investigated and actioned as appropriate. But this is currently not documented. There are currently no protocols in respect of noise and vibration reduction programming operating within the business. Monitoring and investigation are undertaken on an ad hoc basis when the need arises such on receipt of a noise complaint. All plant and equipment is regularly inspected and maintained to ensure they run effectively and efficiently and are in the best condition they can be to prevent noise and vibration, and staff will raise any maintenance work required. A Noise Impact Assessment technical note was produced [ref: B16383-123532-XX-XX-AS-ZA-DH0109 - QUY Noise Impact Assessment January 2024], followed by a noise and vibration management plan [ref: B16383-123532-XX-XX-NN-ZA-DH0118 QUY Noise and Vibration Management Plan July 2024] |  |  | x | Why doesn’t DCWW record noise complaints- I would be wry admitting that noise complaints are actioned but not documented. Unless they mean no records of noise complaints have been made by the public? - added to RFI
|  | II. | Noise and vibration monitoring plan/protocol | But will revisit Noise measurement survey last conducted by Environmental Compliance on 10th May 2016. A Noise Impact Assessment technical note was produced in January 2024 to support the application |  |  |  | x
|  | III. | Noise & vibration complaint response plan/protocol |  |  |  |  | x
|  | IV. | Noise and vibration reduction programme |  |  |  |  | x
| 18 | Techniques to prevent, or where not practicable reduce noise and vibration emissions. Use one or a combination of the following:
|  | a. | Appropriate location of equipment and buildings | For existing plants, the relocation of equipment and building exits or entrances may be restricted by a lack of space or excessive costs. | These are existing plant and there is no change in the current operations of the site to be permitted under IED. The design of the plant did not need to formally record such design considerations. A Noise Impact Assessment technical note was produced [ref: B16383-123532-XX-XX-AS-ZA-DH0109 - QUY Noise Impact Assessment January 2024], followed by a noise and vibration management plan [ref: B16383-123532-XX-XX-NN-ZA-DH0118 QUY Noise and Vibration Management Plan July 2024] |  |  | x
|  | b. | Operational measures – see examples |  | Operational procedures for noise and vibration management are dealt with, and actioned, appropriately especially in respect of noise complaints. General site management varies depending on the plant and equipment on site and the techniques employed on the site. All plant and equipment is regularly inspected and maintained to ensure they run effectively and efficiently and are in the best condition they can be to prevent noise and vibration, and staff will raise any maintenance work required. Equipment is only operated and maintained by trained and competent staff, who are familiar with the equipment they are working with and are able to identify when issues arise. The site has restrictions for noisy operations e.g. deliveries, HGV or tanker movements at certain times and there are speed restrictions and speed calming measures in place to help reduce noise. |  |  | x
|  | c. | Low-noise equipment – see examples |  | Where future equipment is to be replaced, low-noise emitting equipment will be considered and new plant and equipment will be required to meet specific standards across all areas (not just noise). |  |  | x
|  | d. | Noise & vibration control equipment – see examples | VA carried out by external contractors | Applicability may be restricted by a lack of space (for existing plants). |  |  | x
|  | e. | Noise attenuation – see examples | Applicable only to existing plants, as the design of new plants should make this technique unnecessary. For existing plants, the insertion of obstacles may be restricted by a lack of space. | The plant is existing, and noise is not an issue due to proximity of the site to sensitive receptors and other noise emitting activities in the surrounding area. Lack of space on the STC limits the opportunity for control techniques on most of the sites. Noise attentuation will be installed after careful investigation, appropriateness and consideration of placement especially where several complaints have been receive in future. |  |  | x
EMISSIONS TO WATER
| 19 | Optimise water consumption, reduce waste water generation and prevent or where not practicable reduce emissions to soil and water. Use one or a combination of the following:
|  | a. | Water management – see examples | Water consumption is optimised by using measures which may include: — water saving plans (e.g. establishment of water efficiency objectives, flow diagrams and water mass balances); — optimising the use of washing water (e.g. dry cleaning instead of hosing down, using trigger control on all washing equipment); — reducing the use of water for vacuum generation (e.g. use of liquid ring pumps with high boiling point liquids). | Water usage is one of a number of resources carefully managed to minimise consumption. Where water does not need to be of a potable / clean standard final effluent is used as a 'wash water ' system on all sites. This supply will be used for washing down screens, washing down spills, cleaning tanks, foam suppression and carrier water. | x
|  | b. | Water recirculation | Water streams are recirculated within the plant, if necessary after treatment. The degree of recirculation is limited by the water balance of the plant, the content of impurities (e.g. odorous compounds) and/or the characteristics of the water streams (e.g. nutrient content). | As mentioned above the STC recirculates final effluent for washing plant and for a range of non-potable uses. Site drainage directs water landing on impermeable surfaces back to the head of the works to be recirculated through the treatment process. | x
|  | c. | Impermeable surface | Depending on the risks posed by the waste in terms of soil and/or water contamination, the surface of the whole waste treatment area (e.g. waste reception, handling, storage, treatment and dispatch areas) is made impermeable to the liquids concerned. | Large areas of the site close to treatment units are not impermeable. i.e. shingle areas. The areas of the site with the potential sludge spillage is currently undergoing work to cover (or contain in some other way) with an impermeable surface with drainage to the WwTW for treatment via the return liquor pumping station. Further investigations are required to ensure this BAT is fully implemented and compliant. | x | X |  | To ask Anita how to address this - as this links to the CIRIA? - in RFI
|  | d. | Reduce likelihood and impact of tank/vessel overflows and failures – see examples | Tanks designed to relevant codes / specifications at time of construction and built by competent contractors under supervision. High integrity equipment used for sludge transfer and ancilliary assets. Tank and ancilliary condition inspected in line with current maintenance strategy and site operated by competent persons. Secondary containment solution consisting of kerbs, road humps or shallow concrete walls proposed to mitigate against the impact of credible failure modes for storage and transfer assets. Automated Control & Telemetry is included as part of the solution. | Secondary or tertiary containment of tanks, have been constructed at the Site. Appropriate secondary or tertiary containment measures have been investigated to ensure this BAT is fully implemented and compliant. The presence of high-level detectors and overflow alarms on certain tank units have been installed, where appropriate. Any overflow will drain to the works return system for full treatment through the WwTW. An assessment in accordance with CIRIA 736 was undertaken in 2020 to provide the required containment solutions to meet the BAT requirements. Construction of these buds were undertaken, but the Mott MacDonald modelling team have re-modelled and produced a concept design for a potential solution, as part of improvements needed to meet CIRIA 736. DCWW currently provide 110% containment of the largest tank volume. However, modelling has showed that bunds constructed were not suitable for containing sludge in the event of a catastrophic failure and that DCWW should be providing containment for 25% of the total volume as this represents the greater volume. Additional containment measures will be designed and constructed as necessary. The detailed design will refine the concept solution. The containment options report is presented in B16383-123532-ZZ-XX-RP-YB-HY0139 - Queensferry Containment Risk Assessment. The ADBA Risk Assessment is provided in B16564-123532-ZZ-XX-AS-ZA-CI0035 - Queensferry ADBA Assessment October 2024. | x
|  | e. | Roofing of waste storage and treatment areas | Depending on the risks posed by the waste in terms of soil and/or water contamination, waste is stored and treated in covered areas to prevent contact with rainwater and thus minimise the volume of contaminated run- off water. | The site has 3 x 70m3 cake storage bays for the temporary storage of cake. It is considered not necessary to cover the cake bays, based on assessment of risk. The Bioaerosol RA (ref: B16383-123532-XX-XX-AS-ZA-DH0117 - QUY Bioaerosol Risk Assessment September 2024) has identified that the risk from the cake bays is very low due to the volume of cake being low and timescale it is stored on site prior to removal being short - both of which minimises the potential for contaminated runoff from this area. The drainage from the cake bays is diverted to the works return system for full treatment through the adjacent WwTW. The following sludge treatment processes are covered or enclosed (with corresponding site layout plan reference): Digested sludge storage tank (Zone 2) Digester feed tank Digesters 1 & 2 Sludge holding tanks (aka consolidation tanks) 1 & 2 Screened sludge tank Imported sludge tank Returned liquors tank CHP engine Gas holder Dual fuel boilers 1 & 2 Gas oil boiler Drum thickener Centrifuge Biogas flare Standby generator AD condensate trap 1 & 2 Gas bag condensate trap The following sludge treatment processes are open or uncovered Cake (digested) bays Centrifuge feed tank Centrate returns well Thickener returns well Digested sludge tanks Zone 1, Zone 3, Zone 4 and Zone 5 Rotamat (screen) Screenings skip Additional works are underway, as part of this scheme, for odour cover improvements to replace existing covers that are in poor condition. DCWW will make odour cover improvements on the following assets: Sludge import tank Liquor return storage tank Indigenous sludge storage tanks no’s.1 and 2 Digestor feed sludge storage tank New enclosure on imported sludge screening skip There are no plans to cover the digested sludge tanks in Zones 1, 3, 4 & 5 or the centrifuge feed tank. The decision behind this is that the Site is due to be decommissioned before the end of AMP 8, although a date is yet to be confirmed,. Monitoring as required under BAT 6, 7 & 20 for liquor run-off will be undertaken during 2023/24 to enable characterisation and decide whether additional techniques for treatment are necessary. All dewatered sludge cake is transported to the Five Fords Advanced Anaerobic Digestion (AAD) Site, located off Cefn Road to the South-East of Wrexham. The imported cake will be processed through the AAD plant and the derived biogas will then be exported via the Five Fords gas-to-grid installation. The cake will be exported for use as a fertiliser. | x |  | x
|  | f. | Segregation of water streams (being mindful of existing plant constraints) | Each water stream (e.g. surface run-off water, process water) is collected and treated separately, based on the pollutant content and on the combination of treatment techniques. In particular, uncontaminated waste water streams are segregated from waste water streams that require treatment. | Where there is minimal risk of contamination of surface water these areas are drained direct to the surface water system. For areas subject to contamination these areas drain to the works return system for full treatment through the WTW. | x
|  | g. | Adequate drainage infrastructure | The waste treatment area is connected to drainage infrastructure. Rainwater falling on the treatment and storage areas is collected in the drainage infrastructure along with washing water, occasional spillages, etc. and, depending on the pollutant content, recirculated or sent for further treatment. | Where there is minimal risk of contamination of surface water these areas are drained direct to the surface water system. For areas subject to contamination these areas drain to the works return system for full treatment through the WTW. | x
|  | h. | Design and maintenance provisions to allow risk-based leak detection and repair. Minimise use of underground components. | Regular monitoring for potential leakages is risk-based, and, when necessary, equipment is repaired. The use of underground components is minimised. When underground components are used, and depending on the risks posed by the waste contained in those components in terms of soil and/or water contamination, secondary containment of underground components is put in place. | A large proportion of interunit pipework is below ground and leakages are difficult to detect. New pipework is above ground, where possible, and, therefore, any leakages would be visible. Specific areas have been subject to a risk assessment to understand what equipment requires additional containment. A leak detection and repair plan will be developed as part of the EMS. Uncontrolled releases of biogas is monitored by pressure instrumentation of the system pressure relief valves, resulting in alarm conditions to warn the site operations team to take corrective action. The Site currently uses SCADA and telemetry monitoring, combined with daily site walkovers with gas monitoring to ensure emissions to air, from leaks are identified and repaired. During routine maintenance a visual walkover surveys for pipework etc is conducted to check for integrity, corrosions and leaks. Leak detection (methane gas analyser) is also installed on biogas holder/s to ensure any leaks from the inner bag are detected. Any leaks detected on the biogas system would always be fixed immediately by DCWW due to the process safety risk of posed by biogas. Site will be checked and inspected through various routes as per all DCWW assets. Site visual inspections will be completed by DCWW at a defined frequency and recorded in our SAP database alongside all other maintenance activities that are carried out on site. The sites also have a robust 24/7 scada system which includes flow and pressure monitoring where required also providing alarms and trending facilities. The scada system is also connected to DCWW central Smart Hub where all alarms are managed out of hours and responded to accordingly, this aligns with DCWW existing processes and procedures. This is an approach DCWW will be applying to all it’s IED permitted sites and has already been accepted as part of IED permit applications in sites such as Five Fords & Cog Moors WwTW.A leak detection and repair (LDAR) plan will be in place for the Site. |  | x
|  | i. | Appropriate buffer storage capacity (being mindful of existing plant constraints) | Appropriate buffer storage capacity is provided for waste water generated during other than normal operating conditions using a risk-based approach (e.g. taking into account the nature of the pollutants, the effects of downstream waste water treatment, and the receiving environment). The discharge of waste water from this buffer storage is only possible after appropriate measures are taken (e.g. monitor, treat, reuse). | Appropriate secondary or tertiary containment measures have been investigated to ensure this BAT is fully implemented and compliant. DCWW will provide a wastewater and digestate buffer storage plan (listed in regard to BAT 4). The Plan’s purpose is to review, desrcibe and propose site contingency arrangements, and to provide, if necessary, appropriate storage capacity or other appropriate measures to prevent or minimise emissions of wastewater or digestate being discharged off site during any occasions when the receiving wastewater treatment works is in storm overflow operating conditions. It is understood the Plan, if required, will need to include, but not be limited to: *Proposals for additional storage capacity, where necessary, with secondary containment within the site boundary for wastewater and/or other digestate during any occasions when the receiving wastewater treatment works is in storm overflow operating conditions. *Procedures to cease discharges during these conditions. *Calculation of a reasonable contingency capacity of waste water and/or other digestate during any occasions when the receiving wastewater treatment works is in storm overflow operating conditions. *A description and design specification of the buffer storage infrastructure and secondary containment measures. The design shall be completed by an appropriately qualified engineer and secondary containment shall be designed in line with CIRIA C736. *A program of works with timescales for the implementation and construction of the buffer storage. *A preventative maintenance and inspection regime. | x |  |  | DCWW to expand to state there is enough buffer storage (e.g. headroom, additional storage for contingency measures if issues with supply and downstream process 'backing up'. Has further storage space been considered for the future?
| 20 | Treat waste water using a combination of: Please note that any wastewater arises from surface drainage and goes back to the head of the UWWTD regulated WwTW.
Preliminary, primary and general treatment
|  | a. | Equalisation |  | Effluent transferred to adjacent treatment works. The site has preliminary treatment where grit and screenings will be removed and flow measured for full treatment. |  |  | x
|  | b. | Neutralisation |  |  |  |  | x
|  | c. | Physical separation | This happens at the WwTW inlet screens, maccerator and grit removal plant |  | x
Physico-chemical treatment
|  | d. | Adsorption | None of this is required for a coastal or esturial discharge from a WwTW regulated under UWWTR | Effluent transferred to adjacent treatment works. |  |  | x
|  | e. | Distillation/rectification |  |  |  |  | x
|  | f. | Precipitation |  |  |  |  | x
|  | g. | Chemical oxidation |  |  |  |  | x
|  | h. | Chemical reduction |  |  |  |  | x
|  | i. | Evaporation |  |  |  |  | x
|  | j. | Ion exchange |  |  |  |  | x
|  | k. | Stripping |  |  |  |  | x
Biological treatment
|  | l. | Activated sludge process |  | Effluent transferred to adjacent treatment works. |  |  | x
|  | m. | Membrane bioreactor | Secondary treatment filter beds |  | x
Nitrogen removal
|  | n. |  |  | Effluent transferred to adjacent treatment works. |  |  | x
Solids removal
|  | o. | Coagulation and flocculation |  | Effluent transferred to adjacent treatment works. |  |  | x
|  | p. | Sedimentation | Primary settlement and humus tanks |  |  |  | x
|  | q. | Filtration (sand, micro, ultra) | Stone media filter beds |  |  |  | x
|  | r. | Flotation |  |  |  |  | x
BAT-AELs for DIRECT discharges to a receiving waterbody (mg/l)
Table 6.1 and its supporting notes. Monitoring requirements are outlined in BAT 7
|  | TOC | 10.0-60 |  | No direct discharges to water body. Each site has its own permitted determinands. Typically they will all include BOD, COD, suspended solids, with certain sites having: Iron Phosphorous Total Nitrogen Ammonia The majority of the listed parameters in Table 6.1 of BAT 20 are not monitored. Refer to each site's discharge permits for more details of the site's specific determinands. |  |  | x
10-100 for water-based liquid waste
|  | COD (TOC is preferred) | 30-180 |  |  |  |  | x
30-300 for water-based liquid waste
|  | Suspended solids | 5.0-60 |  |  |  |  | x
|  | HOI | 0.5-10 applying to specific waste treatments |  |  |  |  | x
|  | Total N | 1-25 for biological treatment and waste oil re-refining |  |  |  |  | x
10-60 for water-based liquid waste
|  | Total P | 0.3-2 for biological treatment |  |  |  |  | x
1-3 for water-based liquid waste
|  | Phenol | 0.05-0.2 for waste oil re-refining and physio-chemical treatment of waste with CV |  |  |  |  | x
0.05-0.3 for water-based liquid waste
|  | Free CN- | 0.02-0.1 for water-based liquid waste |  |  |  |  | x
|  | AOX | 0.2-1 for water-based liquid waste |  |  |  |  | x
Metals & Metalloids – specific waste treatments as listed in Table 6.1
|  | As | 0.01-0.05 |  | No direct discharges to water body |  |  | x
|  | Cd | 0.01-0.05 |  |  |  |  | x
|  | Cr | 0.01-0.15 |  |  |  |  | x
|  | Cu | 0.05-0.5 |  |  |  |  | x
|  | Pb | 0.05-0.1 |  |  |  |  | x
|  | Ni | 0.05-0.5 |  |  |  |  | x
|  | Hg | 0.5-5 |  |  |  |  | x
|  | Zn | 0.1-1 |  |  |  |  | x
Metals & Metalloids – treatment of water-based liquid waste
|  | As | 0.01-0.1 |  | No direct discharges to water body |  |  | x
|  | Cd | 0.01-0.1 |  |  |  |  | x
|  | Cr | 0.01-0.3 |  |  |  |  | x
|  | Hexavalent Cr [Cr(VI] | 0.01-0.1 |  |  |  |  | x
|  | Cu | 0.05-0.5 |  |  |  |  | x
|  | Pb | 0.05-0.3 |  |  |  |  | x
|  | Ni | 0.05-1 |  |  |  |  | x
|  | Hg | 1.0-10 |  |  |  |  | x
|  | Zn | 0.1-2 |  |  |  |  | x
BAT-AELs for INDIRECT discharges to a receiving waterbody (mg/l)
Table 6.2 and its supporting notes. Monitoring requirements are outlined in BAT 7
|  | HOI | 0.5-10 applying to specific waste treatments |  | It is accepted that testing is not currently completed to BAT requirements. DCWW are developing a wastewater sampling plan and this will be provided within 6 months of permit issue. DCWW will look to implement the plan within 12 months of plan agreement but caution that some more complex elements may take longer, due to lab constraints. A sampling plan is provided [ref:B16383-123532-XX-XX-PR-ZA-DH0133 - QUY SamplingPlan September 2024] |  | x |  | Need to make DCWW aware these are applicable, and need to agree a plan on inventory, and sampling of these indirect emissions. - add as RFI
|  | Free CN- | 0.02-0.1 for water-based liquid waste |  |  |  | x
|  | AOX | 0.2-1 for water-based liquid waste |  |  |  | x
Metals & Metalloids – specific waste treatments as listed in Table 6.2
|  | As | 0.01-0.05 |  | It is accepted that testing is not currently completed to BAT requirements. DCWW are developing a wastewater sampling plan and this will be provided within 6 months of permit issue. DCWW will look to implement the plan within 12 months of plan agreement but caution that some more complex elements may take longer, due to lab constraints. A sampling plan is provided [ref:B16383-123532-XX-XX-PR-ZA-DH0133 - QUY SamplingPlan September 2024] |  | x
|  | Cd | 0.01-0.05 |  |  |  | x
|  | Cr | 0.01-0.15 |  |  |  | x
|  | Cu | 0.05-0.5 |  |  |  | x
|  | Pb | 0.05-0.1 |  |  |  | x
|  | Ni | 0.05-0.5 |  |  |  | x
|  | Hg | 0.5-5 |  |  |  | x
|  | Zn | 0.1-1 |  |  |  | x
Metals & Metalloids – treatment of water-based liquid waste
|  | As | 0.01-0.1 |  | It is accepted that testing is not currently completed to BAT requirements. DCWW are developing a wastewater sampling plan and this will be provided within 6 months of permit issue. DCWW will look to implement the plan within 12 months of plan agreement but caution that some more complex elements may take longer, due to lab constraints. A sampling plan is provided [ref:B16383-123532-XX-XX-PR-ZA-DH0133 - QUY SamplingPlan September 2024] |  | x
|  | Cd | 0.01-0.1 |  |  |  | x
|  | Cr | 0.01-0.3 |  |  |  | x
|  | Hexavalent Cr [Cr(VI] | 0.01-0.1 |  |  |  | x
|  | Cu | 0.05-0.5 |  |  |  | x
|  | Pb | 0.05-0.3 |  |  |  | x
|  | Ni | 0.05-1 |  |  |  | x
|  | Hg | 1.0-10 |  |  |  | x
|  | Zn | 0.1-2 |  |  |  | x
EMISSIONS FROM ACCIDENTS AND INCIDENTS
| 21 | Techniques to prevent or limit the environmental consequences of accidents and incidents, as part of the Accident Management Plan. Use ALL of the following:
|  | a. | Protection measures – see examples | Accient Management plan is existing, but has been updated to meet the BAT standard relevant to the permit application. The AMP will be reviewed on a regular basis. Additional new procedures and updates to relevant existing plans within the system will be undertaken, where necessary, to ensure the requirements and conditions set out within the permit are complied with and gaps filled. | OCNS Security Plan and Accident Management Plan (ref: B16383-123532-XX-XX-PR-OA-HD0106 - QUY Accident Management Plan October 2024). | x
|  | b. | Management of incidental or accidental emissions | A summary of the accident management plan is provided in the Main Supporting Document to the application. An AMP is also provided. | Critical Parameters Board WOF008 and IMS(1) 01 Section 18 and 19; Emergency Procedures EP(3) 01-22; and Accident Management Plan (ref: B16383-123532-XX-XX-PR-OA-HD0106 - QUY Accident Management Plan October 2024). | x
|  | c. | Incident/accident registration and assessment system – see examples | Toolbox talks | Assure Portal | x |  |  | DCWW to provide a summary of this portal - RFI added
MATERIAL EFFICIENCY
| 22 | Use materials efficiently by substituting materials with waste e.g. waste acids/alkalis for pH adjustment, fly ashes for binders |  | Use of WwTW final effluent as opposed to potable water. Dilution water, cooling system & poly make up. Also for site hoses. | The STC uses a by-product of waste water treatment to create biogas which is used to produced heat and power (renewable energy) for the site. Following the digestion process, the digestate is lime treated (depending requirements) to meet the quality requirement set out in the Safe Sludge Matrix and to comply with the HACCP plan. The treated sludge is recycled to agricultural land. Final effluent produced by the wastewater treatment works will be used on the site wherever possible instead of potable water. Details of waste activities is provided in the Main Supporting Document for the permit [ref: B16383-123532-XX-XX-NN-ZA-DH0114 - QUY Main Supporting Document October 2024] | x
ENERGY EFFICIENCY
| 23 | Use energy efficiently by using both of the following techniques:
|  | a. | Energy efficiency plan | Covered by our Welsh Water AMP 7 investment program Energy Plan. This plan isn’t showing an improvement plan at site/facility level, but provides the level of improvement that we are targeting as a company and the metrics used to monitor progress. Our site optimisation team is developing improvement plans for each facility, which is currently ongoing. | Annual reviews of energy efficiency, minimum of four yearly Energy Savings Opportunity Scheme audits. Covered by our Welsh Water AMP 7 investment program Energy Plan. This plan isn’t showing an improvement plan at site/facility level, but provides the level of improvement that we are targeting as a company and the metrics used to monitor progress. Our site optimisation team is developing improvement plans for each facility, which is currently ongoing. | x
|  | b. | Energy balance record | energy consumption and generation | Energy Team report on this daily and with weekly flash reports. As a business we generate equivalent of 20% of our own energy which is generally sold back to the grid. The remaining 80% of electricity brought in is via non-fossil fuel sources. | x
REUSE OF PACKAGING
| 24 | Maximise the reuse of packaging as part of a Residues Management Plan (see BAT 1 XII.) |  | Minimal amounts of packaging. All sent for recovery in preference to disposal with our current hazardous and non hazardous waste tender contractor. | Residues Management Plan (ref: B16383-123532-XX-XX-PE-NA-DH0107 - QUY Residue Management Plan October 2024) will form part of the EMS update required to capture IED activities | x
MECHANICAL TREATMENT OF WASTE (GENERAL BAT)
| 25 | Reduce emissions to air of dust, particulate-bound metals, PCDD/F and dioxin-like PCBs by applying BAT 14d AND using one or a combination of the following techniques:
|  | a. | Cyclone – see S6.1 |  |  |  |  | NA
|  | b. | Fabric filter – see S6.1 |  |  |  |  | NA
|  | c. | Wet scrubbing – see S6.1 |  |  |  |  | NA
|  | d. | Water injection into the shredder |  |  |  |  | NA
BAT-AEL for channelled dust emissions to air from the mechanical treatment of waste (mg/Nm3)
Table 6.3 and its supporting note. Monitoring requirements are outlined in BAT 8
|  | Dust | 2.0-5.0 |  |  |  |  | NA
MECHANICAL TREATMENT OF METAL WASTE BY SHREDDING
| 26 | Improve overall environmental performance and prevent emissions due to accidents and incidents. Use BAT 14g AND ALL of the following techniques:
|  | (a) | Detailed inspection procedure for baled waste before shredding |  |  |  |  | NA
|  | (b) | Remove dangerous items from waste inputs and dispose of them in a safe manner |  |  |  |  | NA
|  | (c) | Treatment of containers accompanied by a declaration of cleanliness |  |  |  |  | NA
| 27 | Prevent deflagrations and reduce emissions from deflagrations. Use technique a. AND ONE OR BOTH of techniques b. and c.
|  | a. | Deflagration management plan with reduction programme, incident review and response protocol |  |  |  |  | NA
|  | b. | Pressure relief dampers |  |  |  |  | NA
|  | c. | Pre-shredding (device) |  |  |  |  | NA
| 28 | Use energy efficiently by keeping the shredder feed stable | [5 empty] | NA
MECHANICAL TREATMENT OF WEEE CONTAINING VFCS AND/OR VHCS
| 29 | Techniques to prevent, or where not practicable reduce emissions of organic compounds to air. Apply BAT 14d AND BAT14h AND technique a. AND ONE OR BOTH of techniques b. and c.
|  | a. | Optimised removal and capture of refrigerants and oils |  |  |  |  | NA
|  | b. | Cryogenic condensation |  |  |  |  | NA
|  | c. | Adsorption |  |  |  |  | NA
BAT-AELs for channelled TVOC and CFC emissions to air from treatment of WEEE containing VFCs and/or VHCs (mg/Nm3)
Table 6.4. Monitoring requirements are outlined in BAT 8
|  | TVOC | 3.0-15 |  |  |  |  | NA
|  | CFCs | 0.5-10 |  |  |  |  | NA
| 30 | Prevent emissions due to explosions when treating WEEE containing VFCs and/or VHCs. Use EITHER of the following techniques:
|  | a. | Inert atmosphere e.g. N2 |  |  |  |  | NA
|  | b. | Forced ventilation |  |  |  |  | NA
MECHANICAL TREATMENT OF WASTE WITH CALORIFIC VALUE
| 31 | Reduce emissions to air of organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
|  | a. | Adsorption – see S6.1 |  |  |  |  | NA
|  | b. | Biofilter – see S6.1 |  |  |  |  | NA
|  | c. | Thermal oxidation – see S6.1 |  |  |  |  | NA
|  | d. | Wet scrubbing – see S6.1 |  |  |  |  | NA
BAT-AEL for channelled TVOC emissions to air from the mechanical treatment of waste with calorific value (mg/Nm3)
Table 6.5 and its supporting note. Monitoring requirements are outlined in BAT 8
|  | TVOC | 10.0-30.0 |  |  |  |  | NA
MECHANICAL TREATMENT OF WEEE CONTAINING MERCURY
| 32 | Reduce mercury emissions to air by collecting them at source, sending them to abatement and carrying out adequate monitoring. This includes ALL of the following:
|  | Equipment is enclosed, under negative pressure and connected to a LEV system | [5 empty] | NA
|  | Waste gas treated using dedusting techniques – see examples – followed by adsorption on activated carbon | [5 empty] | NA
|  | Monitoring of waste gas treatment efficiency | [5 empty] | NA
|  | Mercury levels measured at least weekly within treatment and storage areas | [5 empty] | NA
BAT-AEL for channelled mercury (Hg) emissions to air from the mechanical treatment of WEEE containing mercury (µg/Nm3)
Table 6.6. Monitoring requirements are outlined in BAT 8
|  | Hg | 2.0-7.0 |  |  |  |  | NA
BIOLOGICAL TREATMENT OF WASTE (GENERAL BAT)
| 33 | Reduce odour emissions and improve overall environmental performance by selecting the waste input (to ensure its suitability for biological treatment). See also BAT 2 |  |  | Covered in BAT2 - The waste input is based on the waste codes defined in the permit. Waste inputs to the site and described in more detail in the main supporting document and include in the OMP |  |  | x
| 34 | Reduce emissions to air of dust, organic compounds and odorous compounds (including H2S & NH3) by using one or a combination of the following techniques:
|  | a. | Adsorption – see S6.1 | Unless otherwise stated, the BAT conclusions presented in Section 3 apply to the biological treatment of waste, and in addition to the general BAT conclusions in Section 1. | No abatement technologies used on site. |  |  | x
|  | b. | Biofilter – see S6.1 |  | The OCU uses biofilter but the OCU is currently not operational. Further investigation, modelling and testing by Olfasense has been completed and the results are presented in the OIA with the accompanying OMP identifying monitoring requirements and mitigation measures for the management of odour. There are two OCUs that serve the STC, there are located adjacent to the imported sludge works (ref 9, A09 of Figure 1.1) and located adjacent to the sludge thickener building (ref 10, A10 of Figure 1.1). The OCUs are designed to treat air from these processes. The Site currently does not have any operational odour control units (OCUs). However, works are underway as part of the Queensferry IED Odour Control Scheme to install new OCU’s, to replace the current non-functioning OCUs, to comply with the IED and BAT requirements. The provision of new odour control treatment system - AWT Dry (Peacemaker chlorinated shale) system (similar to the existing odour unit on site as part of the wastewater treatment) at the works to treat combined extracted odorous airflow from the following locations: Sludge import tank Liquor return storage tank Imported sludge screen and screening skip Thickener building including direct extraction from existing drum thickener Indigenous sludge storage tanks no’s.1 and 2 Digestor feed sludge storage tank The OCUs will have an odour removal efficiency of 99.5% for both systems. The extracted odours combine from the above locations to new odour abatement plants to give reduced odour emission from a 315mm x 5m high stack, and total flow rate of 2,470m3/hr – 15m/s at a maximum of 1,000 ou/m3. Treated odour streams are discharged to the environment through the OCU stacks and monitored hourly to ensure the absence of odorous compounds. |  | x
|  | c. | Fabric filter – see S6.1. |  | No abatement technologies used on site. |  |  | x
|  | d. | Thermal oxidation – see S6.1 |  | No abatement technologies used on site. |  |  | x
|  | e. | Wet scrubbing – see S6.1 |  | No abatement technologies used on site. |  |  | x
BAT-AEL for channelled NH3, odour, dust and TVOC emissions to air from the biological treatment of waste (mg/Nm3) (ouE/m3)
Table 6.7 and its supporting notes. Monitoring requirements are outlined in BAT 8
|  | NH3 | 0.3-20 |  | Monitoring requirements are outlined in the Odour Management Plan provided as doc ref B16383-123532-XX-XX-PR-ZA-DH0129 - QUY Odour Management Plan October 2024. and as per other DCWW IED sites |  |  | x
|  | Odour | 200-1000 |  |  | x
|  | Dust | 2.0-5.0 |  | Not applicable as it is not a dusty operation |  |  | x
|  | TVOC | 5.0-40 |  | DCWW confirm that they will characterise emissions from the odour control units in line with BAT 3 to demonstrate if TVOC and HCI are present in the waste gas stream. Where TVOC and HCI are identified as relevant in the waste gas streams then DCWW will continue to monitor these emissions in line with BAT requirements |  |  | x
| 35 | Reduce the generation of waste water and reduce water usage by using ALL of the following:
|  | a. | Segregation of water streams (see also BAT 19f) | Uncontminated surface water is segregated. Generally the liquid and solid waste streams of EWC 19 06 05 (liqour) and 19 06 06 (digestate) are not segregated for recovery under SUiAR but can be in the event of breakdown or maintenance. | See BAT 19f Areas of site with the potential for contamination of water (e.g. cake loading area where leachate may be generated) will always drain back to the wastewater treatment works for full treatment, whilst areas that are free from contamination (e.g. roofs, footpaths etc) will drain to the site’s surface water drainage system. |  |  | x
|  | b. | Water recirculation | Final effluent from wastewater treatment process is used for polymer make up, sludge dilution, belt press washwater and sludge cooling system | Flows on PVSS Final effluent generated by the wastewater treatment works wherever possible instead of potable water.is used as a pressure returned effluent as already highlighted in earlier BAT reviews. All wastewater flows from the STC are 'recycled' for full treatment through the WTW. | x
|  | c. | Minimisation of the generation of leachate | No leachate generation | The final product (digested sludge) is dewatered to at least 25%ds as this is deemed the optimal dry solid percentage - balancing power and poly consumption to achieve this target. |  |  | x
BIOLOGICAL TREATMENT OF WASTE: AEROBIC METHODS
| 36 | Reduce emissions to air and improve overall environmental performance by monitoring and/or controlling key waste and process parameters. Include following elements:
|  | Waste input characteristics e.g. C to N ratio, particle size | [5 empty] | NA
|  | Temperature and moisture content within windrows (Moisture monitoring not needed for enclosed processes where H&S issues have been identified) | [5 empty] | NA
|  | Aeration of the windrow | [5 empty] | NA
|  | Windrow porosity, height and width | [5 empty] | NA
| 37 | Reduce diffuse emissions to air of dust, odour and bioaerosols from open-air treatment steps. Use ONE OR BOTH of the following techniques:
|  | a. | Use of semi-permeable membrane covers |  |  |  |  | NA
|  | b. | Adaptation of operations to the meteorological conditions |  |  |  |  | NA
BIOLOGICAL TREATMENT OF WASTE: ANAEROBIC METHODS
Faye | 38 | Reduce emissions to air and improve overall environmental performance by monitoring and/or controlling key waste and process parameters. Include following elements:
Implement a manual and/or automatic monitoring system to:
|  | Ensure a stable digester operation |  | Weekly samples and daily monitoring and control of feed Digester Help Sheet (local document) & PVSS | The anaerobic digestion process is fully automated using key process instrumentation (temperature profiles, feed volume and dry solids, pressure, foam level and biogas production and quality) to effectively monitor and optimise key process parameters to ensure stable digester operation. This includes automatic fail-safe systems which will revert the digester into a safe and stable condition in the event of an incident or episode of instability (e.g. If foam levels reach a critical level the digester feed and mixing systems would be inhibited - requiring an operator to reset). The key controls are HACCP control points - RT and temperature - recorded daily and kept within the PVSS system / standard spreadsheet. Other key determinands are also recorded to ensure healthy digestion process. Imports are managed via a production planning process to ensure sites are fed in stable and controlled manner each week. The digesters and auxiliary plant contain instrumentation that will provide early warning of a loss of containment or explosion risk, with appropriate fail-safe operation within the software or hardwired. These include dual-level instrumentation within the digester headspace, as well as level switches in the digester overspill chamber to warn of blockage in the downstream pipework. Digester headspace also contains pressure instrumentation which warns of over pressurisation of the digesters. This is backed up by dual pressure and vacuum relief valves on the digester roof which ventilate to atmosphere. A foam-radar in the digester headspace, combined with an automatic anti-foam dosing system ensures foam does not escape through the biogas off-take pipework, or the PRV's. There is pressure monitoring throughout the biogas system, as well as leak detection on the gas holder and gas detection within buildings to warn of an explosion risk. These systems are linked to fast-acting slam-shut valves which isolate all fuels to combustion plant to remove the risk of a fire or explosion. Digesters and the gas holder are controlled by PRVs, pressure sensors and alarms on whessoe valves. Pressure is monitored through SCADA. | x
|  | Minimise operational difficulties and associated odour emissions |  | Weekly samples and daily monitoring and control of feed Digester Help Sheet (local document) & PVSS |  | x
|  | Provide sufficient early warning of system failures |  | All equipment monitored 24hrs a day by the PVSS SCADA system. And alarms attached to relevent equipment PVSS |  | x
|  | Windrow porosity, height and width | [5 empty] | x
Monitoring and/or control of key waste and process parameters – examples below:
|  | pH and alkalinity of the digester feed |  | Sampled weekly | Digester Help Sheet (local document) pH expected range 7.6 to 8.5 Alkalinity expected range 7000 to 10000 | x
|  | Digester operating temperature |  | Monitored continuously and controlled by a cooling system. With automated features, i.e. if digester temperature is too high, digester feed will stop | PVSS & local Availability sheet The internal temperature of the digesters is approximately 38-40 oC Each digester is fitted with 3No. temperature probes in order to monitor/maintain digester operating temperature. When temperature in the digester is above / below the set‐temperature, more/ less cooling water would need to be passed through the sludge cooler in order to maintain a constant temperature in the digester | x
|  | Hydraulic and organic loading rates of the digester feed |  | Monitored through flows and sampling | Digester Help Sheet (local document) & PVSS Dry solids expected ranges of 4 to 5.5% Volatile solids expected ranges 55 to 70% | x
|  | Volatile fatty acids and NH3 concentrations within digester & digestate |  | Sampled weekly | Digester Help Sheet (local document) Volatile fatty acids expected range 1000 to 2000 Ammonia expected range 2500 to 3300 | x
|  | Biogas quantity, composition (e.g. H2S) and pressure |  | PVSS measures biogas volumes through flow meters. Also measured on CHP engines. Composition measured by handheld gas monitor weekly. Pressure continuously measured on PVSS | Digester Help Sheet (local document) & PVSS Biogas composition ranges: - Methane 58 to 70% - Carbon Dioxide 30 to40% - Oxygen <1% - H2S <100ppm | x
|  | Liquid and foam levels in the digester |  | Continuously measured on PVSS | PVSS | x
MECHANICAL BIOLOGICAL TREATMENT (MBT) OF WASTE
| 39 | Reduce emissions to air. Generally applicable to new plants, existing plants may have layout constraints. Use BOTH of the following techniques:
|  | a. | Segregation of the waste gas streams (refer to inventory described in BAT 3) |  |  |  |  | NA
|  | b. | Recirculation of waste gas. Waste gas treatment is described in BAT 34 and recirculation in BAT 35. |  |  |  |  | NA
PHYSICO-CHEMICAL TREATMENT OF SOLID AND/OR PASTY WASTE
| 40 | Improve overall environmental performance by monitoring the waste input as part of the waste pre-acceptance and acceptance procedures. See also BAT 2.
Monitoring the waste input
|  | Content of organics, oxidising agents, metals, salts, odorous compounds | [5 empty] | X
|  | H2 formation potential upon mixing of flue-gas treatment residues/ashes with water | [5 empty] | X
| 41 | Reduce emissions to air of dust, organic compounds and NH3 by applying BAT 14d AND using one or a combination of the following techniques:
|  | a. | Adsorption – see S6.1 |  |  |  |  | X
|  | b. | Biofilter – see S6.1 |  |  |  |  | X
|  | c. | Fabric filter – see S6.1. |  |  |  |  | X
|  | d. | Wet scrubbing – see S6.1 |  |  |  |  | X
BAT-AEL for channelled NH3, odour, dust and TVOC emissions to air from the physico-chemical treatment of solid and/or pasty waste (mg/Nm3)
Table 6.8. Monitoring requirements are outlined in BAT 8
|  | Dust | 2.0-5.0 |  |  |  |  | X
RE-REFINING OF WASTE OIL
| 42 | Improve overall environmental performance by monitoring the waste input as part of the waste pre-acceptance and acceptance procedures. See also BAT 2.
Monitoring the waste input
|  | Chlorinated compounds e.g. solvents or PCBs | [5 empty] | NA
| 43 | Reduce quantity of waste sent for disposal by using ONE OR BOTH of the following techniques:
|  | a. | Material recovery e.g. organic residues in asphalt products |  |  |  |  | NA
|  | b. | Energy recovery |  |  |  |  | NA
| 44 | Reduce emissions to air of organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
|  | a. | Adsorption – see S6.1 |  |  |  |  | NA
|  | b. | Thermal oxidation – see S6.1 |  |  |  |  | NA
|  | c. | Wet scrubbing – see S6.1 |  |  |  |  | NA
The BAT-AEL for TVOC emissions to air set in Section 4.5 (below) applies.
Monitoring requirements are outlined in BAT 8
PHYSICO-CHEMICAL TREATMENT OF WASTE WITH CALORIFIC VALUE
| 45 | Reduce emissions to air of organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
|  | a. | Adsorption – see S6.1 |  |  |  |  | X
|  | b. | Cryogenic condensation – see S6.1 |  |  |  |  | X
|  | c. | Thermal oxidation – see S6.1 |  |  |  |  | X
|  | d. | Wet scrubbing – see S6.1 |  |  |  |  | X
The BAT-AEL for TVOC emissions to air set in Section 4.5 (below) applies.
Monitoring requirements are outlined in BAT 8
REGENERATION OF SPENT SOLVENTS
| 46 | Improve overall environmental performance by using ONE OR BOTH of the following techniques:
|  | a. | Material recovery (by evaporation from distillation residues) |  |  |  |  | NA
|  | b. | Energy recovery e.g. using distillation residues |  |  |  |  | NA
| 47 | Reduce emissions to air of organic compounds by applying BAT 14d AND using a combination of the following techniques:
|  | a. | Recirculation of process off-gases in a steam boiler. Avoid generating PCBs and/or PCDD/Fs |  |  |  |  | NA
|  | b. | Adsorption – see S6.1 |  |  |  |  | NA
|  | c. | Thermal oxidation – see S6.1. Avoid generating PCBs and/or PCDD/Fs |  |  |  |  | NA
|  | d. | Condensation or cryogenic condensation |  |  |  |  | NA
|  | e. | Wet scrubbing – see S6.1 |  |  |  |  | NA
The BAT-AEL for TVOC emissions to air set in Section 4.5 (below) applies.
Monitoring requirements are outlined in BAT 8
BAT-AEL FOR EMISSIONS OF ORGANIC COMPOUNDS TO AIR – SECTION 4.5
(RE-REFINING OF WASTE OIL)
(PHYSICO-CHEMICAL TREATMENT OF WASTE WITH CV)
(REGENERATION OF SPENT SOLVENTS)
BAT-AEL for channelled TVOC emissions to air from the re-refining of waste oil, physico-chemical treatment of waste with calorific value and regeneration of spent solvents (mg/Nm3)
Table 6.9 and its supporting note. Monitoring requirements are outlined in BAT 8
|  | TVOC | 5.0-30 |  |  |  |  | NA
THERMAL TREATMENT OF SPENT ACTIVATED CARBON, WASTE CATALYSTS AND EXCAVATED CONTAMINATED SOIL
| 48 | Improve overall environmental performance by using ALL of the following techniques:
|  | a. | Heat recovery from the furnace off-gas e.g. for preheating combustion air or steam generation |  |  |  |  | NA
|  | b. | Indirectly fired furnace i.e. avoids contact between the furnace contents and the burner flue-gases. Note applicability constraints. |  |  |  |  | NA
|  | c. | Process-integrated techniques to reduce emissions to air – see examples |  |  |  |  | NA
| 49 | Reduce emissions to air of HCl, HF, dust and organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
|  | a. | Cyclone – see S6.1 |  |  |  |  | NA
|  | b. | Electrostatic precipitator (ESP) – see S6.1 |  |  |  |  | NA
|  | c. | Fabric filter – see S6.1 |  |  |  |  | NA
|  | d. | Wet scrubbing – see S6.1 |  |  |  |  | NA
|  | e. | Adsorption – see S6.1 |  |  |  |  | NA
|  | f. | Condensation – see S6.1 |  |  |  |  | NA
|  | g. | Thermal oxidation – see S6.1 |  |  |  |  | NA
Note supporting text for BAT 49g (thermal oxidation)
Monitoring requirements are outlined in BAT 8. No BAT-AELs have been set for this BATc.
WATER WASHING OF EXCAVATED CONTAMINATED SOIL
| 50 | Reduce emissions to air of dust and organic compounds from the storage, handling and washing steps by applying BAT 14d AND using one or a combination of the following techniques:
|  | a. | Adsorption – see S6.1 |  |  |  |  | NA
|  | b. | Fabric filter – see S6.1 |  |  |  |  | NA
|  | c. | Wet scrubbing – see S6.1 |  |  |  |  | NA
Monitoring requirements are outlined in BAT 8. No BAT-AELs have been set for this BATc.
WATER WASHING OF EXCAVATED CONTAMINATED SOIL
| 51 | Reduce emissions to air of PCBs and organic compounds and improve overall environmental performance by using ALL of the following techniques:
|  | a. | Coating of the storage and treatment areas – see examples |  |  |  |  | NA
|  | b. | Implementation of staff access rules to prevent dispersion of contamination – see examples |  |  |  |  | NA
|  | c. | Optimised equipment cleaning and drainage – see examples |  |  |  |  | NA
|  | d. | Control and monitoring of emission to air – see examples |  |  |  |  | NA
|  | e. | Disposal of waste treatment residues – see examples |  |  |  |  | NA
|  | f. | Recovery of solvent when solvent washing is used |  |  |  |  | NA
Monitoring requirements are outlined in BAT 8. No BAT-AELs have been set for this BATc.
TREATMENT OF WATER-BASED LIQUID WASTE
| 52 | Improve overall environmental performance by monitoring the waste input as part of the waste pre-acceptance and acceptance procedures. See also BAT 2.
Monitoring the waste input
|  | Bioeliminability e.g. BOD, BOD-COD ratio, Zahn-Wellens test, biological inhibition potential |  |  | As per BAT 2 |  |  | x
|  | Feasibility of emulsion breaking e.g. lab testing | [5 empty] | x
| 53 | Reduce emissions to air of HCl, NH3 and organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
|  | a. | Adsorption – see S6.1 |  |  |  |  | x
|  | b. | Biofilter – see S6.1 |  | As per BAT 14 and 34 |  | x
|  | c. | Thermal oxidation – see S6.1. |  |  |  |  | x
|  | d. | Wet scrubbing – see S6.1 |  | No wet scrubbing - biofilters used on site |  |  | x
BAT-AELs for channelled HCl and TVOC emissions to air from the treatment of water-based liquid waste (mg/Nm3)
Table 6.10 and its supporting notes. Monitoring requirements are outlined in BAT 8
|  | HCl | 1.0-5.0 |  |  |  |  | x
|  | TVOC | 3.0-20 |  |  |  |  | x

## WT BAT Conclusions
BATc number |  | Issue | Description of the techiques in place and how Operator intends to meet each standard | Supporting Evidence (Reference Documents) | Anticipated Compliance Date
[5 empty] | Now | 2022 | N/A
OVERALL ENVIRONMENTAL PERFORMANCE
1 | Environment Management System (EMS) – ALL of the following:
| I. | Management commitment
| II. | Environmental policy development including CI of performance
| III. | Planning and implementing procedures & targets in conjunction with financial planning & investment
| IV. | Implementation of procedures
(a) Structure & responsibility
(b) Recruitment, training, awareness & competence
(c) Communication
(d) Employee involvement
(e) Documentation
(f) Effective process control
(g) Maintenance programmes
(h) Emergency preparedness & response
(i) Safeguarding compliance with environmental legislation
| V. | Checking performance and taking corrective action
(a) Monitoring & measurement
(b) Corrective and preventive action
(c) Maintenance of records
(d) Independent (where practicable) internal or external EMS auditing
| VI. | Senior management review of EMS
| VII. | Following development of cleaner technologies
| VIII. | Whole life cycle considerations when designing a new plant i.e. impacts from eventual decommissioning and throughout its operating life
| IX. | Regular sectoral bench marking
| X. | Waste stream management (BAT 2)
| XI. | Inventory of waste water & waste gas streams (BAT 3)
| XII. | Residues Management Plan – S6.5
| XIII. | Accident Management Plan – S6.5
| XIV. | Odour Management Plan (BAT 12)
| XV. | Noise & Vibration Management Plan (BAT 17)
2 | Improving overall environmental performance – ALL of the following:
| a. | Set up and implement waste characterisation & pre-acceptance procedures
| b. | Set up and implement waste acceptance procedures
| c. | Set up and implement a waste tracking system & inventory
| d. | Set up and implement an output quality management system
| e. | Ensure waste segregation
| f. | Ensure waste compatibility prior to mixing or blending
| g. | Sort solid incoming waste – S6.4
3 | Establish and maintain a waste water and waste gas inventory as part of the EMS - ALL of the following:
Information on characteristics of waste and waste treatment processes
| (i)(a) | simplified process flow sheets showing emission sources
| (i)(b) | Process-integrated and waste water/waste gas treatment descriptions including performance
Information on characteristics of waste water streams
| (ii)(a) | Mean and variability of:
Flow
pH
Temperature
Conductivity
| (ii)(b) | Mean concentration, load and variability of:
Total suspended solids
COD/TOC
Nitrogen species
Phosphorous
Metals
Priority substances/micropollutants
Any other relevant compounds
| (ii)(c) | Bioeliminability data (see BAT 52):
BOD
BOD to COD ratio
Zahn-Wellens test
Biological inhibition potential
Information on characteristics of waste gas streams
| (iii)(a) | Mean and variability of:
Flow
temperature
| (iii)(b) | Mean concentration, load and variability of relevant substances:
Organic compounds
POPs e.g. PCBs
Any other relevant compounds
| (iii)(c) | Flammability
Lower and Higher Explosive Limits
Reactivity
| (iii)(d) | Presence of other substances that may affect the gas treatment system or plant safety:
O2
N2
Water vapour
Dust
4 | Reducing environmental risk associated with waste storage – ALL of the following:
| a. | Optimised storage location
| b. | Adequate storage capacity
| c. | Safe storage operation
| d. | Separate area for storage & handling of packaged hazardous waste
5 | Set up and implement procedures to reduce the environmental risk associated with handling and transfer of waste - include following elements:
Carried out by competent staff
Duly documented, validated and verified
Spill prevention, detection and mitigation measures
Take precautions when mixing or blending wastes
Procedures are risk-based and consider likelihood of accidents, incidents and their environmental impact
MONITORING
6 | Relevant emissions to water: monitor key process parameters at key locations
Key process parameters
Waste water flow
pH
Temperature
Conductivity
BOD
Other process parameters
Key monitoring locations
Pre-treatment inlet and/or outlet
Final treatment inlet
Discharge point (to the environment)
Other location
7 | Monitoring emissions to water (refer to table)
Monitoring parameters depend on waste treatment process(es) involved
8 | Monitoring emissions to air (refer to table)
Monitoring parameters depend on waste treatment process(es) involved
9 | Monitoring diffuse emissions of organic compounds to air from processes involving solvents. Use one or a combination of the following:
| a | Measurement – S6.2 descriptions
| b | Emissions factor calculation
| c | Mass balance calculation
10 | Periodically monitor odour emissions where nuisance is expected and/or has been substantiated (monitoring frequency is outlined in BAT 12)
Use EN standards e.g. 13725 or 16841
Use equivalent methods e.g. ISO / national / international monitoring standards
11 | Annual monitoring for:
- Water, energy and raw materials
- Generation of residues and waste water
EMISSIONS TO AIR
12 | Set up, implement and review an Odour Management Plan (as part of the site EMS) where nuisance is expected and/or has been substantiated. Include ALL of the following:
Protocol containing actions and timelines
Protocol for conducting odour monitoring (BAT 10)
Protocol for response to odour incidents/complaints
Odour prevention and reduction programme
13 | Techniques to prevent, or where not practicable reduce odour emissions. Use one or a combination of the following:
| a. | Minimising residence times (open systems only)
| b. | Use chemical treatment (N/A if desired output is hampered)
| c. | Optimising aerobic treatment – see examples. Refer to BAT 36 for wastes other than water-based liquid waste.
14 | Techniques to prevent, or where not practicable reduce diffuse emissions to air, in particular of dust, organic compounds and odour. Use one or a combination of the following:
| a. | Minimising potential diffuse emission sources – see examples
| b. | Select and use high-integrity equipment – see examples
| c. | Corrosion prevention – see examples
| d. | Containment, collection and treatment of diffuse emissions – see examples
| e. | Dampening (with water or fog)
| f. | Maintenance – see examples
| g. | Cleaning of waste treatment and storage areas – see examples
| h. | Leak Detection And Repair (LDAR) programme for organics – S6.2
15 | Use flaring only for safety reasons or non-routine operating conditions (OTNOC). Use both of the following:
| a. | Correct plant design – see examples
| b. | Plant management including gas system balancing and advanced process control
16 | Reduce emissions to air when flaring is unavoidable. Use both of the following:
| a. | Correct design of flaring devices – see examples
| b. | Monitoring and recording as part of flare management – see examples
NOISE AND VIBRATIONS
17 | Set up, implement, and regularly review a Noise and Vibration Management Plan (as part of the EMS) where nuisance is expected and/or has been substantiated. Include ALL of the following:
| I. | Protocol with actions and timelines
| II. | Noise and vibration monitoring plan/protocol
| III. | Noise & vibration complaint response plan/protocol
| IV. | Noise and vibration reduction programme
18 | Techniques to prevent, or where not practicable reduce noise and vibration emissions. Use one or a combination of the following:
| a. | Appropriate location of equipment and buildings
| b. | Operational measures – see examples
| c. | Low-noise equipment – see examples
| d. | Noise & vibration control equipment – see examples
| e. | Noise attenuation – see examples
EMISSIONS TO WATER
19 | Optimise water consumption, reduce waste water generation and prevent or where not practicable reduce emissions to soil and water. Use one or a combination of the following:
| a. | Water management – see examples
| b. | Water recirculation
| c. | Impermeable surface
| d. | Reduce likelihood and impact of tank/vessel overflows and failures – see examples
| e. | Roofing of waste storage and treatment areas
| f. | Segregation of water streams (being mindful of existing plant constraints)
| g. | Adequate drainage infrastructure
| h. | Design and maintenance provisions to allow risk-based leak detection and repair. Minimise use of underground components.
| i. | Appropriate buffer storage capacity (being mindful of existing plant constraints)
20 | Treat waste water using a combination of:
Preliminary, primary and general treatment
| a. | Equalisation
| b. | Neutralisation
| c. | Physical separation
Physico-chemical treatment
| d. | Adsorption
| e. | Distillation/rectification
| f. | Precipitation
| g. | Chemical oxidation
| h. | Chemical reduction
| i. | Evaporation
| j. | Ion exchange
| k. | Stripping
Biological treatment
| l. | Activated sludge process
| m. | Membrane bioreactor
Nitrogen removal
| n. | Nitrification/denitrification (where biological treatment used)
Solids removal
| o. | Coagulation and flocculation
| p. | Sedimentation
| q. | Filtration (sand, micro, ultra)
| r. | Flotation
BAT-AELs for DIRECT discharges to a receiving waterbody (mg/l)
Table 6.1 and its supporting notes. Monitoring requirements are outlined in BAT 7
| TOC | 10.0-60
10-100 for water-based liquid waste
| COD (TOC is preferred) | 30-180
30-300 for water-based liquid waste
| Suspended solids | 5.0-60
| HOI | 0.5-10 applying to specific waste treatments
| Total N | 1-25 for biological treatment and waste oil re-refining
10-60 for water-based liquid waste
| Total P | 0.3-2 for biological treatment
1-3 for water-based liquid waste
| Phenol | 0.05-0.2 for waste oil re-refining and physio-chemical treatment of waste with CV
0.05-0.3 for water-based liquid waste
| Free CN- | 0.02-0.1 for water-based liquid waste
| AOX | 0.2-1 for water-based liquid waste
Metals & Metalloids – specific waste treatments as listed in Table 6.1
| As | 0.01-0.05
| Cd | 0.01-0.05
| Cr | 0.01-0.15
| Cu | 0.05-0.5
| Pb | 0.05-0.1
| Ni | 0.05-0.5
| Hg | 0.5-5
| Zn | 0.1-1
Metals & Metalloids – treatment of water-based liquid waste
| As | 0.01-0.1
| Cd | 0.01-0.1
| Cr | 0.01-0.3
| Hexavalent Cr [Cr(VI] | 0.01-0.1
| Cu | 0.05-0.5
| Pb | 0.05-0.3
| Ni | 0.05-1
| Hg | 1.0-10
| Zn | 0.1-2
BAT-AELs for INDIRECT discharges to a receiving waterbody (mg/l)
Table 6.2 and its supporting notes. Monitoring requirements are outlined in BAT 7
| HOI | 0.5-10 applying to specific waste treatments
| Free CN- | 0.02-0.1 for water-based liquid waste
| AOX | 0.2-1 for water-based liquid waste
Metals & Metalloids – specific waste treatments as listed in Table 6.2
| As | 0.01-0.05
| Cd | 0.01-0.05
| Cr | 0.01-0.15
| Cu | 0.05-0.5
| Pb | 0.05-0.1
| Ni | 0.05-0.5
| Hg | 0.5-5
| Zn | 0.1-1
Metals & Metalloids – treatment of water-based liquid waste
| As | 0.01-0.1
| Cd | 0.01-0.1
| Cr | 0.01-0.3
| Hexavalent Cr [Cr(VI] | 0.01-0.1
| Cu | 0.05-0.5
| Pb | 0.05-0.3
| Ni | 0.05-1
| Hg | 1.0-10
| Zn | 0.1-2
EMISSIONS FROM ACCIDENTS AND INCIDENTS
21 | Techniques to prevent or limit the environmental consequences of accidents and incidents, as part of the Accident Management Plan. Use ALL of the following:
| a. | Protection measures – see examples
| b. | Management of incidental or accidental emissions
| c. | Incident/accident registration and assessment system – see examples
MATERIAL EFFICIENCY
22 | Use materials efficiently by substituting materials with waste e.g. waste acids/alkalis for pH adjustment, fly ashes for binders
ENERGY EFFICIENCY
23 | Use energy efficiently by using both of the following techniques:
| a. | Energy efficiency plan
| b. | Energy balance record
REUSE OF PACKAGING
24 | Maximise the reuse of packaging as part of a Residues Management Plan (see BAT 1 XII.)
MECHANICAL TREATMENT OF WASTE (GENERAL BAT)
25 | Reduce emissions to air of dust, particulate-bound metals, PCDD/F and dioxin-like PCBs by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Cyclone – see S6.1
| b. | Fabric filter – see S6.1
| c. | Wet scrubbing – see S6.1
| d. | Water injection into the shredder
BAT-AEL for channelled dust emissions to air from the mechanical treatment of waste (mg/Nm3)
Table 6.3 and its supporting note. Monitoring requirements are outlined in BAT 8
| Dust | 2.0-5.0
MECHANICAL TREATMENT OF METAL WASTE BY SHREDDING
26 | Improve overall environmental performance and prevent emissions due to accidents and incidents. Use BAT 14g AND ALL of the following techniques:
| (a) | Detailed inspection procedure for baled waste before shredding
| (b) | Remove dangerous items from waste inputs and dispose of them in a safe manner
| (c) | Treatment of containers accompanied by a declaration of cleanliness
27 | Prevent deflagrations and reduce emissions from deflagrations. Use technique a. AND ONE OR BOTH of techniques b. and c.
| a. | Deflagration management plan with reduction programme, incident review and response protocol
| b. | Pressure relief dampers
| c. | Pre-shredding (device)
28 | Use energy efficiently by keeping the shredder feed stable
MECHANICAL TREATMENT OF WEEE CONTAINING VFCS AND/OR VHCS
29 | Techniques to prevent, or where not practicable reduce emissions of organic compounds to air. Apply BAT 14d AND BAT14h AND technique a. AND ONE OR BOTH of techniques b. and c.
| a. | Optimised removal and capture of refrigerants and oils
| b. | Cryogenic condensation
| c. | Adsorption
BAT-AELs for channelled TVOC and CFC emissions to air from treatment of WEEE containing VFCs and/or VHCs (mg/Nm3)
Table 6.4. Monitoring requirements are outlined in BAT 8
| TVOC | 3.0-15
| CFCs | 0.5-10
30 | Prevent emissions due to explosions when treating WEEE containing VFCs and/or VHCs. Use EITHER of the following techniques:
| a. | Inert atmosphere e.g. N2
| b. | Forced ventilation
MECHANICAL TREATMENT OF WASTE WITH CALORIFIC VALUE
31 | Reduce emissions to air of organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1
| b. | Biofilter – see S6.1
| c. | Thermal oxidation – see S6.1
| d. | Wet scrubbing – see S6.1
BAT-AEL for channelled TVOC emissions to air from the mechanical treatment of waste with calorific value (mg/Nm3)
Table 6.5 and its supporting note. Monitoring requirements are outlined in BAT 8
| TVOC | 10.0-30.0
MECHANICAL TREATMENT OF WEEE CONTAINING MERCURY
32 | Reduce mercury emissions to air by collecting them at source, sending them to abatement and carrying out adequate monitoring. This includes ALL of the following:
Equipment is enclosed, under negative pressure and connected to a LEV system
Waste gas treated using dedusting techniques – see examples – followed by adsorption on activated carbon
Monitoring of waste gas treatment efficiency
Mercury levels measured at least weekly within treatment and storage areas
BAT-AEL for channelled mercury (Hg) emissions to air from the mechanical treatment of WEEE containing mercury (µg/Nm3)
Table 6.6. Monitoring requirements are outlined in BAT 8
| Hg | 2.0-7.0
BIOLOGICAL TREATMENT OF WASTE (GENERAL BAT)
33 | Reduce odour emissions and improve overall environmental performance by selecting the waste input (to ensure its suitability for biological treatment). See also BAT 2
34 | Reduce emissions to air of dust, organic compounds and odorous compounds (including H2S & NH3) by using one or a combination of the following techniques:
| a. | Adsorption – see S6.1
| b. | Biofilter – see S6.1
| c. | Fabric filter – see S6.1.
| d. | Thermal oxidation – see S6.1
| e. | Wet scrubbing – see S6.1
BAT-AEL for channelled NH3, odour, dust and TVOC emissions to air from the biological treatment of waste (mg/Nm3) (ouE/m3)
Table 6.7 and its supporting notes. Monitoring requirements are outlined in BAT 8
| NH3 | 0.3-20
| Odour | 200-1000
| Dust | 2.0-5.0
| TVOC | 5.0-40
35 | Reduce the generation of waste water and reduce water usage by using ALL of the following:
| a. | Segregation of water streams (see also BAT 19f)
| b. | Water recirculation
| c. | Minimisation of the generation of leachate
BIOLOGICAL TREATMENT OF WASTE: AEROBIC METHODS
36 | Reduce emissions to air and improve overall environmental performance by monitoring and/or controlling key waste and process parameters. Include following elements:
Waste input characteristics e.g. C to N ratio, particle size
Temperature and moisture content within windrows (Moisture monitoring not needed for enclosed processes where H&S issues have been identified)
Aeration of the windrow
Windrow porosity, height and width
37 | Reduce diffuse emissions to air of dust, odour and bioaerosols from open-air treatment steps. Use ONE OR BOTH of the following techniques:
| a. | Use of semi-permeable membrane covers
| b. | Adaptation of operations to the meteorological conditions
BIOLOGICAL TREATMENT OF WASTE: ANAEROBIC METHODS
38 | Reduce emissions to air and improve overall environmental performance by monitoring and/or controlling key waste and process parameters. Include following elements:
Implement a manual and/or automatic monitoring system to:
Ensure a stable digester operation
Minimise operational difficulties and associated odour emissions
Provide sufficient early warning of system failures
Windrow porosity, height and width
Monitoring and/or control of key waste and process parameters – examples below:
pH and alkalinity of the digester feed
Digester operating temperature
Hydraulic and organic loading rates of the digester feed
Volatile fatty acids and NH3 concentrations within digester & digestate
Biogas quantity, composition (e.g. H2S) and pressure
Liquid and foam levels in the digester
MECHANICAL BIOLOGICAL TREATMENT (MBT) OF WASTE
39 | Reduce emissions to air. Generally applicable to new plants, existing plants may have layout constraints. Use BOTH of the following techniques:
| a. | Segregation of the waste gas streams (refer to inventory described in BAT 3)
| b. | Recirculation of waste gas. Waste gas treatment is described in BAT 34 and recirculation in BAT 35.
PHYSICO-CHEMICAL TREATMENT OF SOLID AND/OR PASTY WASTE
40 | Improve overall environmental performance by monitoring the waste input as part of the waste pre-acceptance and acceptance procedures. See also BAT 2.
Monitoring the waste input
Content of organics, oxidising agents, metals, salts, odorous compounds
H2 formation potential upon mixing of flue-gas treatment residues/ashes with water
41 | Reduce emissions to air of dust, organic compounds and NH3 by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1
| b. | Biofilter – see S6.1
| c. | Fabric filter – see S6.1.
| d. | Wet scrubbing – see S6.1
BAT-AEL for channelled NH3, odour, dust and TVOC emissions to air from the physico-chemical treatment of solid and/or pasty waste (mg/Nm3)
Table 6.8. Monitoring requirements are outlined in BAT 8
| Dust | 2.0-5.0
RE-REFINING OF WASTE OIL
42 | Improve overall environmental performance by monitoring the waste input as part of the waste pre-acceptance and acceptance procedures. See also BAT 2.
Monitoring the waste input
Chlorinated compounds e.g. solvents or PCBs
43 | Reduce quantity of waste sent for disposal by using ONE OR BOTH of the following techniques:
| a. | Material recovery e.g. organic residues in asphalt products
| b. | Energy recovery
44 | Reduce emissions to air of organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1
| b. | Thermal oxidation – see S6.1
| c. | Wet scrubbing – see S6.1
The BAT-AEL for TVOC emissions to air set in Section 4.5 (below) applies.
Monitoring requirements are outlined in BAT 8
PHYSICO-CHEMICAL TREATMENT OF WASTE WITH CALORIFIC VALUE
45 | Reduce emissions to air of organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1
| b. | Cryogenic condensation – see S6.1
| c. | Thermal oxidation – see S6.1
| d. | Wet scrubbing – see S6.1
The BAT-AEL for TVOC emissions to air set in Section 4.5 (below) applies.
Monitoring requirements are outlined in BAT 8
REGENERATION OF SPENT SOLVENTS
46 | Improve overall environmental performance by using ONE OR BOTH of the following techniques:
| a. | Material recovery (by evaporation from distillation residues)
| b. | Energy recovery e.g. using distillation residues
47 | Reduce emissions to air of organic compounds by applying BAT 14d AND using a combination of the following techniques:
| a. | Recirculation of process off-gases in a steam boiler. Avoid generating PCBs and/or PCDD/Fs
| b. | Adsorption – see S6.1
| c. | Thermal oxidation – see S6.1. Avoid generating PCBs and/or PCDD/Fs
| d. | Condensation or cryogenic condensation
| e. | Wet scrubbing – see S6.1
The BAT-AEL for TVOC emissions to air set in Section 4.5 (below) applies.
Monitoring requirements are outlined in BAT 8
BAT-AEL FOR EMISSIONS OF ORGANIC COMPOUNDS TO AIR – SECTION 4.5
(RE-REFINING OF WASTE OIL)
(PHYSICO-CHEMICAL TREATMENT OF WASTE WITH CV)
(REGENERATION OF SPENT SOLVENTS)
BAT-AEL for channelled TVOC emissions to air from the re-refining of waste oil, physico-chemical treatment of waste with calorific value and regeneration of spent solvents (mg/Nm3)
Table 6.9 and its supporting note. Monitoring requirements are outlined in BAT 8
| TVOC | 5.0-30
THERMAL TREATMENT OF SPENT ACTIVATED CARBON, WASTE CATALYSTS AND EXCAVATED CONTAMINATED SOIL
48 | Improve overall environmental performance by using ALL of the following techniques:
| a. | Heat recovery from the furnace off-gas e.g. for preheating combustion air or steam generation
| b. | Indirectly fired furnace i.e. avoids contact between the furnace contents and the burner flue-gases. Note applicability constraints.
| c. | Process-integrated techniques to reduce emissions to air – see examples
49 | Reduce emissions to air of HCl, HF, dust and organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Cyclone – see S6.1
| b. | Electrostatic precipitator (ESP) – see S6.1
| c. | Fabric filter – see S6.1
| d. | Wet scrubbing – see S6.1
| e. | Adsorption – see S6.1
| f. | Condensation – see S6.1
| g. | Thermal oxidation – see S6.1
Note supporting text for BAT 49g (thermal oxidation)
Monitoring requirements are outlined in BAT 8. No BAT-AELs have been set for this BATc.
WATER WASHING OF EXCAVATED CONTAMINATED SOIL
50 | Reduce emissions to air of dust and organic compounds from the storage, handling and washing steps by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1
| b. | Fabric filter – see S6.1
| c. | Wet scrubbing – see S6.1
Monitoring requirements are outlined in BAT 8. No BAT-AELs have been set for this BATc.
WATER WASHING OF EXCAVATED CONTAMINATED SOIL
51 | Reduce emissions to air of PCBs and organic compounds and improve overall environmental performance by using ALL of the following techniques:
| a. | Coating of the storage and treatment areas – see examples
| b. | Implementation of staff access rules to prevent dispersion of contamination – see examples
| c. | Optimised equipment cleaning and drainage – see examples
| d. | Control and monitoring of emission to air – see examples
| e. | Disposal of waste treatment residues – see examples
| f. | Recovery of solvent when solvent washing is used
Monitoring requirements are outlined in BAT 8. No BAT-AELs have been set for this BATc.
TREATMENT OF WATER-BASED LIQUID WASTE
52 | Improve overall environmental performance by monitoring the waste input as part of the waste pre-acceptance and acceptance procedures. See also BAT 2.
Monitoring the waste input
Bioeliminability e.g. BOD, BOD-COD ratio, Zahn-Wellens test, biological inhibition potential
Feasibility of emulsion breaking e.g. lab testing
53 | Reduce emissions to air of HCl, NH3 and organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1
| b. | Biofilter – see S6.1
| c. | Thermal oxidation – see S6.1.
| d. | Wet scrubbing – see S6.1
BAT-AELs for channelled HCl and TVOC emissions to air from the treatment of water-based liquid waste (mg/Nm3)
Table 6.10 and its supporting notes. Monitoring requirements are outlined in BAT 8
| HCl | 1.0-5.0
| TVOC | 3.0-20