## 1.Risk assessment
1.1 | Source
For the purposes of the ADBA Assessment, assets containing sludge have been listed only
| Name | Number | Physical properties | Maximum quantity (above ground) | units | Storage | Flammability | Corrosive | Ecotoxicity (based on LD and quantity) | Hazard rating
| Sludge Holding Tank (Screened Sludge Storage Tanks) (partially below ground) | 2 | Raw Sludge | 75 | m3 | Concrete | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Digester Feed Tank (Thickened Sludge Tank) (partially below ground) | 1 | Raw Sludge | 75 | m3 | Concrete | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Digester (partially below ground) | 2 | Digested Sludge | 1420 | m3 | Concrete | Methane produced is flammable Digestate isn't flammable | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Imported Screened Sludge Tank (underground) | 1 | Raw Sludge | 0 | m3 | Concrete | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Digested Sludge Holding Tank 1 (partially below ground) | 1 | Digested Sludge | 1334 | m3 | Concrete | Methane produced is flammable Digestate isn't flammable | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Digested Sludge Holding Tank 2 (partially below ground) | 1 | Digested Sludge | 1442 | m3 | Concrete | Methane produced is flammable Digestate isn't flammable | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Digested Sludge Holding Tanks | 2 | Digested Sludge | 468 | m3 | GFS | Methane produced is flammable Digestate isn't flammable | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Centrifuge feed tank | 1 | Digested Sludge | 159 | m3 | GFS | Methane produced is flammable Digestate isn't flammable | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
| Cake Bays | 3 | Raw Cake | 70 | m3 | Existing impermeable hardstanding | Low | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | L
| Sludge Holding Tanks (3 Lanes) (partially below ground) | 3 | Digested Sludge | 100 | m3 | Concrete | Methane produced is flammable Digestate isn't flammable | Low | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) | M
[8 empty] | Overall | M
|  |  | Total Volume | 7446 | m3
|  |  | 25% Volume | 1861.5 | m3 | 25% volume to be taken forward.
|  |  | 110% Largest Tank (Digested Sludge Holding Tank 2) | 1586.2 | m3
1.2 | Pathway and Receptor
Figure 1.1 - Source
Permit boundary
Site boundary
Figure 1.2 - Pathway
Figure 1.3 Receptor
| Pathway - the route from primary containment to receptor (extent of loss of containment) |  | Time of concentration/ duration of source outside containment |  | Hazard - Transport potential | Receptor | Hazard - Damage potential
| Tanks are surrounded by, grass, permeable hardstanding stone and impermeable concrete. Based on available ground information, soil is permeable and will act as a pathway |  | Direct contamination but over an extended period of time |  | M | Watercourse and bodies
| If permeable area gets saturated (high groundwater or due to the area flooding as the treatment works is in Flood Zone 3) or becomes blocked with sludge, areas will act as impermeable and transport sludge downstream and towards the River Dee. |  | Direct contamination but over an extended period of time |  | M | Groundwater - contaminated through percolation through soil or through fluctuating tidal groundwater level Site is not located within 250m of a Source Protection Zone (SPZ), however the entire site and locality area (surface water) and within a Secondary A aquifer. Over a very long period, can contaminate river through groundwater base flow underground | M
| Tidally fluctuating groundwater |  | Direct contamination but over an extended period of time |  | M | Sludge storage within 50m of a watcourse that discharges into the River Dee, which is designated as a Site of Special Scientific Interest (SSSI) and Special Area of Conservation (SAC). | H
| Existing underground services - ductwork, troughs, pipework. |  | Direct contamination but over an extended period of time |  | L | Local environment including grassy area - through overland flow from uncontrolled spill. <5m away | M
| There is impermeable concrete surfacing on site If inventory is lost or cascaded onto the road (saturated permeable ground), sludge will be transported downstream along the road surface into the road gullies and into the site drainage system which is connected to soakaways next to abandoned gas holder. These soakaways infiltrate into the soil. |  | Minutes - hours |  | M | WWTW - internal drainage system returns effluent to the head of the works prior to discharge into the River Dee | M
| If the soakaways get blocked, each soakaway has an overflow to the drainage system (liquor return). |  | Minutes - hours |  | M | Habitation
|  |  | Overall |  | M | Third party land (Bromborough Plastics Ltd) 100m from digesters | M
Other
[6 empty] | River Dee SSSI within 250m of the site | H
[6 empty] | Overall | H
| Combination of Hazards | MMH
| Overall risk rating for zone (Ciria 736) | High
1.3 | Frequency of loss of containment
In terms of likelihood of a loss of containment, CIRIA 736 provides these guidelines on quantifying the likelihood...
To derive the likelihood for your site, firstly, using the completed risk descriptions and any additional risks identified at your site ask yourself how often will the risk occur and cause a loss of primary containment.
Secondly, consider any mitigation (see the examples provided in the table starting below row 50 for guidance) and apply the reduced likelihood.
Finally, select the likelihood by applying the fact that the highest likelihood gives the site's overall likelihood.
| Failure mode | Description | Existing consequence and mitigation measure | [6 empty] | Annual probability of loss of containment | Rating
| Operational failure - tank (partial) | Overfilling/overflow of tank Foaming | Digesters have high level overflows which connect to the pipes feeding the digested sludge holding tanks when levels within the tanks are too high. Each digester spills 80 - 100m3 of digestate to the digested sludge holding tanks each day. The filling of the zones is controlled manually by operational staff. Zones are filled on a zone by zone basis. Based on the digester feed pumps, the gravity flow rate to the digested sludge holding tanks would be 8-10l/s (4-5l/s per pump). Operational staff reported that there have been overfilling/overflow cases, but in the past and not recently. Based on discussions with operational staff, there are no high level overflows within the sludge holding tanks. There are however ultrasonic depth monitors. The level within the tanks are monitored by ultrasonic level sensors, but not linked to Scada or alarmed. Sludge supplied to the digesters displace the existing digestate and sludge overflows. All tanks are also covered. In the unlikely event when there is an overflow (overflows blocked and non working volume is filled), the volume lost would be minimal (Assumed <22m3 based on hourly pump flow rate of the thickener pumps) as the pumps can be inhibited automatically or by operators present onsite. Total loss of containment is unlikely (partial loss of containment would be more likely to occur but unlikely) Foaming is a very general failure mode for digesters. Foaming could occupy up to 2m of height within the digesters. Otherwise, automated and operator safeguards are in place to control or inhibit the process if there is a foaming risk. Total loss of containment is not credible when considering overflowing or foaming of the tank (partial loss of containment would be more likely to occur but is still very unlikely). | [6 empty] | 1 in 100 to 1 in 1 Million | M
| Structural failure - tank (catastrophic) | Catastrophic failure due to significant external damage Potential to lose total volume if mixer pipework fails/break off of tank - has been a failure mode for digesters in the past | Tanks are located above ground. In the case of significant damage above ground during operation or maintenance, the total volume contained above ground could be lost. It is not credible for the tanks to fail catastrophically structurally as the tank is fit for purpose. The tanks were originally designed and constructed to hold hydrolysed sludge and have been operating with no notable concerns. Structural failure of the tank would mainly be through cracks. In the case of significant cracks forming above ground, the volume contained above ground would seep through the cracks. Due to operational presence on site, large drops in levels in the tanks and significant leaks above ground would be noticed. Significant cracks (>6mm) below/above ground would also be easily spotted if tank is inspected. Cracks, especially significant cracks (>6mm), would be easily spotted when the tank is inspected. During refurbishment of the digester roof, operations inspected the concrete tanks and it was in a good condition with no signs of reinforcement corrosion, surface damage or significant cracks. The roof has failed in the past (lifted). Proportion of volume could be lost, but from discussions with operations, no loss of containment was experienced during time when roof lifted as the site is manned. The tanks could lose their full inventory if the pipe connections to the tank fail/break off and fail catastrophically, causing a rupture/hole in the tank, through which the total inventory is lost as mixer pipework is located near the bottom of the digester tanks. This pipework is supported and the connections in the tank wall are cast in with puddle flanges and hydrophilic water bars so this type of failure is not a credible scenario. The tanks are not hydraulically linked so failure of one tank would not result in the loss of containment of additional tanks. | [6 empty] | > 1 in 1 Million | L
| Structural failure - tank (partial) | Most likely through cracks formed in concrete Most critical cracks would be large cracks at low level along the side of the tank walls or tank base. Cracks would need to be large >6mm to allow for sludge to pass through the crack freely. General screens at WwTW are 6-10mm, thus cracks would need to be in the same range to allow for sludge to pass freely. Roof failure | Tanks are located above ground. Any significant loss of containment, would spill above ground. Structural failure of tanks would mainly be through cracks. In the case of significant cracks forming above ground, the volume contained above ground would seep through the cracks . If the cracks are significant (>6mm), the tank could potentially lose the above ground volume over a long period of time. This would be identified promptly by operators and the process inhibited immediately. The tanks have been designed as double skinned tanks and constructed to the appropriate code for water retaining concrete structures or steel structures so this could only reasonably be assumed to occur if the tanks were operated well in excess of their design life without appropriate maintenance or any refurbishment. As the site is manned, large drops in levels in the tanks and significant leaks above ground would be noticed. Significant cracks below/above ground would also be easily spotted if tanks are inspected throughout their design life. Partial loss of containment from cracks is still highly unlikely and safeguards are in place to mitigate the impact of such a leak. | [6 empty] | > 1 in 1 Million | L
| Structural failure - pipework (catastrophic) | Loss of containment due to failure of above ground connecting pipework and rising mains | In the extremely unlikely event where the above ground pipework or valves fail completely, the total above ground volume could be lost, if the valves are not closed by operational staff or tanks are not drained down to limit loss of containment. As the site is generally manned, the digester feed pumps and mixing pumps would be shut down immediately and valves closed by operational staff if the pipes were to fail. In the case where critical pipework fails and valves cannot mitigate the spillage, the digester could lose its full volume. Due to the makeup of some of the tanks (glass reinforced steel), total loss of containment is considered a rare but credible scenario. Partial loss of containment is however more likely but still considered an unlikely occurance. | [6 empty] | > 1 in 1 Million | L
| Structural failure - pipework (partial) | Loss of containment most likely to occur where there are weak points in the pipework - Most likely through failures where pipe connects with the structure, bolts/sealant at pipe flanges/valves or along any pipe pitting. Weak point could be created through either human damage (during maintenance/operation), erosion (high velocities and silt content within the pipe) or environmental (corrosion) Valve failure/seizure | Majority of pipework and connections are located above ground (stainless steel). Some of the pipework is located below ground or within the chambers below ground. If loss of containment occurs underground (through leaks, joints and seals), sludge will percolate into the soil at a slow rate over a long period. If significant leaks, localised wet areas will be present above ground. If loss of containment occurs above ground through leaks or damage to pipework, due to the permeable stone around tank, sludge will also percolate into the soil at a slow rate over a long period. Due to operational presence on site, significant leaks (above or below) ground would be noticed and loss of containment would be mitigated through operational measures (closing of valves). Pipework was replaced in 2018 and there have been no known leaks from new stainless steel pipework. Due to the impermeable external surfacing around the concrete bunds, the majority of the sludge from leaks at valves/mixers would be contained within the hardstanding area within the bund and, if significant, cascade into the gullies within the chambers and ultimately to the head of the works. The quantities of sludge involved is not expected to have an adverse impact on the wastewater treatment process. Due to the makeup of some of the tanks (glass reinforced steel), total loss of containment is considered a rare but credible scenario. Partial loss of containment is however more likely but still considered an unlikely occurance. | [6 empty] | 1 in 100 to 1 in 1 Million | M
| Vehicular impact (partial to catastrophic) | Impact from vehicles - damage to pipes or tank causing loss of containment | No known vehicle impacts - but no barrier/protection Vehicles could potentially impact and damage tanks which are located above ground. Vehicular impact could cause some damage to the tank (cracking), if significant, proportion of above ground volume could be lost. Vehicle is however unlikely to damage underground sections of tanks or displace any liquid within them. Total loss of containment could occur if the vehicle impact causes significant damage to the tank. High speed impact unlikely, but vehicle could damage pipework connected to tank (mixer pump) and cause a significant hole in the tank at low level. Could impact a potential weak point. Total loss of containment is therefore not deemed to be a credible scenario. | [6 empty] | 1 in 100 to 1 in 1 Million | M
| Vandalism | Vandalism of infrastructure - damage to pipes or tank causing loss of containment | No known vandalism to tanks or pipework - CCTV cameras on site. Thefts in the past based on comments from operators but not damage to any of the assets on site. If vandalism damage were to occur, total loss of containment is unlikely. Could occur if significant damage or theft of mixer pumps and pipework. Partial loss of containment would be more likely to occur if slight damage was done. | [6 empty] | 1 in 100 to 1 in 1 Million | M
| Flooding | River flooding - Flood zone 3 - damage to pipes or tank causing loss of containment | The site is located within a low risk zone for flooding (between 1 and 0.1%) from the the River Dee which is a SSSI. The area according to the government long term flood risk website (https://check-long-term-flood-risk.service.gov.uk/map?easting=352884&northing=238182&map=RiversOrSea) is at high risk of flooding, which a chance of flooding of greater than 3.3% each year. There are no areas of the proposed permit boundary indicated as being affected by groundwater flooding. No flooding has been reported/recorded by the operators Even if flooding occurred, tanks will not be damaged and full volume of sludge will not be lost. There could be a potential for the flood water to be contaminated. The flood water could enter the below ground chambers around the digester and has the potential to get contaminated. | [6 empty] | 1 in 100 to 1 in 1 Million | M
*Site is manned. Probability and frequency thus reduced
| Frequency of loss of containment (Ciria 736) | M
1.4 | Overall zone hazard rating
| Overall zone hazard rating (Ciria 736) | High
1.5 | Containment required
| Containment required | Class 3
Railway
River Dee
Grassy area & trees - potential ecology
102m
206m
77m
A road
115m
68m
Grassy area & trees - potential ecology
third party land
100m
50m
Watercourse that discharges into the River Dee
Watercourse that discharges into the River Dee

## 2.Total vol. - Mitigation
2.1 | Catastrophic failure - modes (loss of containment)
| Risk | Cause | Existing consequence and mitigation measure | Existing zone risk rating | Proposed Mitigation | Risk rating after mitigation
|  | Operational failure - tank (partial) | Digesters have high level overflows which connect to the pipes feeding the digested sludge holding tanks when levels within the tanks are too high. Each digester spills 80 - 100m3 of digestate to the digested sludge holding tanks each day. The filling of the zones is controlled manually by operational staff. Zones are filled on a zone by zone basis. Based on the digester feed pumps, the gravity flow rate to the digested sludge holding tanks would be 8-10l/s (4-5l/s per pump). Operational staff reported that there have been overfilling/overflow cases, but in the past and not recently. Based on discussions with operational staff, there are no high level overflows within the sludge holding tanks. There are however ultrasonic depth monitors. The level within the tanks are monitored by ultrasonic level sensors, but not linked to Scada or alarmed. Sludge supplied to the digesters displace the existing digestate and sludge overflows. All tanks are also covered. In the unlikely event when there is an overflow (overflows blocked and non working volume is filled), the volume lost would be minimal (Assumed <22m3 based on hourly pump flow rate of the thickener pumps) as the pumps can be inhibited automatically or by operators present onsite. Total loss of containment is unlikely (partial loss of containment would be more likely to occur but unlikely) Foaming is a very general failure mode for digesters. Foaming could occupy up to 2m of height within the digesters. Otherwise, automated and operator safeguards are in place to control or inhibit the process if there is a foaming risk. Total loss of containment is not credible when considering overflowing or foaming of the tank (partial loss of containment would be more likely to occur but is still very unlikely). | M | Operational staff reported that there have been overfilling/overflow cases of the sludge holding tanks, but in the past and not recently. Based on discussions with operational staff, there are no high level overflows within the sludge holding tanks. There are however ultrasonic depth monitors. The level within the tanks are monitored by ultrasonic level sensors, but not linked to Scada or alarmed. Foaming could occur, if a mixer fails or the digestate composition is different. As foaming cannot be completely mitigated through anti-foaming measures, secondary containment should be provided for a proportion of digester volume. Possible foaming volume to be accommodated is assumed to be 1m of each digester. In the unlikely event that tank loses significant containment above ground sludge will cascade towards the access road and eventually into the drainage system, based on the site topography. Only competent and trained staff operate the site. The zone is robust and safe provided the permeable areas around the digesters (gravel/stone) is replaced with impermeable hardstanding to remove the pathway to the ground and containment is provided to contain the foaming volume within the site. | L
|  | Structural failure - tank (catastrophic) | Tanks are located above ground. In the case of significant damage above ground during operation or maintenance, the total volume contained above ground could be lost. It is not credible for the tanks to fail catastrophically structurally as the tank is fit for purpose. The tanks were originally designed and constructed to hold hydrolysed sludge and have been operating with no notable concerns. Structural failure of the tank would mainly be through cracks. In the case of significant cracks forming above ground, the volume contained above ground would seep through the cracks. Due to operational presence on site, large drops in levels in the tanks and significant leaks above ground would be noticed. Significant cracks (>6mm) below/above ground would also be easily spotted if tank is inspected. Cracks, especially significant cracks (>6mm), would be easily spotted when the tank is inspected. During refurbishment of the digester roof, operations inspected the concrete tanks and it was in a good condition with no signs of reinforcement corrosion, surface damage or significant cracks. The roof has failed in the past (lifted). Proportion of volume could be lost, but from discussions with operations, no loss of containment was experienced during time when roof lifted as the site is manned. The tanks could lose their full inventory if the pipe connections to the tank fail/break off and fail catastrophically, causing a rupture/hole in the tank, through which the total inventory is lost as mixer pipework is located near the bottom of the digester tanks. This pipework is supported and the connections in the tank wall are cast in with puddle flanges and hydrophilic water bars so this type of failure is not a credible scenario. The tanks are not hydraulically linked so failure of one tank would not result in the loss of containment of additional tanks. | L | If severe damage does occur, operational staff can isolate the tank and drain it down as an emergency response, reducing the loss of containment as they will be in the vicinity of the tank. To reduce the likelihood of loss of containment, the tanks should be structurally inspected on an annual basis by a competent engineer. The tanks should then be refurbished if necessary. Ultrasonic meters in tanks should be alarmed if there is a significant and unanticipated drop in level to mitigate any significant loss of containment. To allow for some loss of containment due to catastrophic failure or significant mixer connection leakage (pre-failure), secondary containment to allow for minimum of 500mm of digester height volume loss until tank is drained down by operational staff. In the case of valve seizure (double jeopardy) - Allow for an additional 250mm of volume loss (750mm in total). The zone is robust and safe provided the permeable areas around the digesters (gravel/stone) is replaced with impermeable hardstanding to remove the pathway to the ground and secondary containment is provided to contain the potential volume loss of the digester within the site. | L
|  | Structural failure - tank (partial) | Tanks are located above ground. Any significant loss of containment, would spill above ground. Structural failure of tanks would mainly be through cracks. In the case of significant cracks forming above ground, the volume contained above ground would seep through the cracks . If the cracks are significant (>6mm), the tank could potentially lose the above ground volume over a long period of time. This would be identified promptly by operators and the process inhibited immediately. The tanks have been designed as double skinned tanks and constructed to the appropriate code for water retaining concrete structures or steel structures so this could only reasonably be assumed to occur if the tanks were operated well in excess of their design life without appropriate maintenance or any refurbishment. As the site is manned, large drops in levels in the tanks and significant leaks above ground would be noticed. Significant cracks below/above ground would also be easily spotted if tanks are inspected throughout their design life. Partial loss of containment from cracks is still highly unlikely and safeguards are in place to mitigate the impact of such a leak. | L | In the event that tank loses containment above ground, through structural failure (cracks), sludge would weep through the cracks at a very slow rate. The volume would slowly flow down the side of the tank and gather around the tank. To reduce the likelihood of loss of containment, the tanks should be structurally inspected on an annual basis by a competent engineer. The tanks should then be refurbished if necessary. Ultrasonic meters in tanks should be alarmed if there is a significant and unanticipated drop in level to mitigate any significant loss of containment. The zone is robust and safe provided the permeable areas around the tanks are replaced with impermeable hardstanding to remove the pathway to the ground. Associated drainage would connect to the inlet works. The tanks should be inspected on at least an annual basis by a competent engineer in addition to the current maintenance strategy. This can be undertaken during the sludge plant's annual maintenance and inspection shutdown. No further mitigation is considered to be necessary. | L
|  | Structural failure - pipework (catastrophic) | In the extremely unlikely event where the above ground pipework or valves fail completely, the total above ground volume could be lost, if the valves are not closed by operational staff or tanks are not drained down to limit loss of containment. As the site is generally manned, the digester feed pumps and mixing pumps would be shut down immediately and valves closed by operational staff if the pipes were to fail. In the case where critical pipework fails and valves cannot mitigate the spillage, the digester could lose its full volume. Due to the makeup of some of the tanks (glass reinforced steel), total loss of containment is considered a rare but credible scenario. Partial loss of containment is however more likely but still considered an unlikely occurance. | L | If catastrophic failure of the above ground pipework occurs (i.e. rising main pipe failure), the pumps have the necessary pressure controls to switch off the pumps to minimise the loss of containment. The volume contained in the pipe length should still be contained. Additional secondary containment is not proposed and volume is assumed will be able to be accommodated in the new hardstanding area around the tank and pipework within the drainage system. The zone is robust and safe provided the permeable areas around the tanks are replaced with impermeable hardstanding to remove the pathway to the ground. Associated drainage would connect to the inlet works. The above ground pipework should continue to be regularly inspected during daily and weekly inspections to enable proactive maintenance when required. Below ground pipework and chambers should be inspected on an annual basis to check their integrity. | L
|  | Structural failure - pipework (partial) | Majority of pipework and connections are located above ground (stainless steel). Some of the pipework is located below ground or within the chambers below ground. If loss of containment occurs underground (through leaks, joints and seals), sludge will percolate into the soil at a slow rate over a long period. If significant leaks, localised wet areas will be present above ground. If loss of containment occurs above ground through leaks or damage to pipework, due to the permeable stone around tank, sludge will also percolate into the soil at a slow rate over a long period. Due to operational presence on site, significant leaks (above or below) ground would be noticed and loss of containment would be mitigated through operational measures (closing of valves). Pipework was replaced in 2018 and there have been no known leaks from new stainless steel pipework. Due to the impermeable external surfacing around the concrete bunds, the majority of the sludge from leaks at valves/mixers would be contained within the hardstanding area within the bund and, if significant, cascade into the gullies within the chambers and ultimately to the head of the works. The quantities of sludge involved is not expected to have an adverse impact on the wastewater treatment process. Due to the makeup of some of the tanks (glass reinforced steel), total loss of containment is considered a rare but credible scenario. Partial loss of containment is however more likely but still considered an unlikely occurance. | M | The above ground pipework is located within the bunded area so will have secondary containment. Based on experience the volume that could be lost due to above ground pipework leaks is minimal. Significant leaks would be spotted by operational staff during their daily inspection (site is also manned) and repaired and any loss of containment mitigated. The volume lost to leaks would be able to be contained in the new hardstanding area around the tanks (replacing the permeable stone) and drainage pipework. No secondary containment required. Sludge would seep through the leaks at a very slow rate. The volume would slowly flow down the side of the pipe and gather around the pipework. The actual volume lost would be minimal. In the unlikely event that there is significant loss of containment through pipework above ground, based on topography and the type of inventory, loss of containment would be limited to the hardstanding area around the pipework and the stone area around the digesters. Jetting from leaks in the pipework shall be contained within the bunded area. The zone is robust and safe provided the permeable areas around the tanks is replaced with impermeable hardstanding to remove the pathway to the ground. Associated drainage would connect to the inlet works. The above ground pipework should continue to be regularly inspected during daily and weekly inspections to enable proactive maintenance when required. Below ground pipework and chambers should be inspected on an annual basis to check their integrity. | L
|  | Vehicular impact (partial to catastrophic) | No known vehicle impacts - but no barrier/protection Vehicles could potentially impact and damage tanks which are located above ground. Vehicular impact could cause some damage to the tank (cracking), if significant, proportion of above ground volume could be lost. Vehicle is however unlikely to damage underground sections of tanks or displace any liquid within them. Total loss of containment could occur if the vehicle impact causes significant damage to the tank. High speed impact unlikely, but vehicle could damage pipework connected to tank (mixer pump) and cause a significant hole in the tank at low level. Could impact a potential weak point. Total loss of containment is therefore not deemed to be a credible scenario. | M | The existing measures mitigate any potential impacts from vehicles within the site and potential damage which could lead to loss of containment. There is however a risk of vehicles impacting the digesters from the road adjacent to the site. Additional vehicular impact protection is recommended to be installed and temporary fencing replaced with permanent fencing. | L
|  | Vandalism | No known vandalism to tanks or pipework - CCTV cameras on site. Thefts in the past based on comments from operators but not damage to any of the assets on site. If vandalism damage were to occur, total loss of containment is unlikely. Could occur if significant damage or theft of mixer pumps and pipework. Partial loss of containment would be more likely to occur if slight damage was done. | M | If pipes and the tank get damaged, because it is operated on a daily basis with operational staff present, the risk of loss of containment is low. If there are any signs of damage due to vandalism operators will fix any damage first. No mitigation measures proposed, existing measures deemed adequate. | L
|  | Flooding | The site is located within a low risk zone for flooding (between 1 and 0.1%) from the the River Dee which is a SSSI. The area according to the government long term flood risk website (https://check-long-term-flood-risk.service.gov.uk/map?easting=352884&northing=238182&map=RiversOrSea) is at high risk of flooding, which a chance of flooding of greater than 3.3% each year. There are no areas of the proposed permit boundary indicated as being affected by groundwater flooding. No flooding has been reported/recorded by the operators Even if flooding occurred, tanks will not be damaged and full volume of sludge will not be lost. There could be a potential for the flood water to be contaminated. The flood water could enter the below ground chambers around the digester and has the potential to get contaminated. | M | The containment that will be constructed to comply with IED regulations will also likely reduce the flood risk of the treatment works site from the River Dee. During optioneering, the risk of negatively impacting flood risk elsewhere needs to be mitigated. If the treatment works site is still classified as a flood zone following containment construction, procedures need to be agreed and adopted in the event of the treatment works site flooding to minimise pollutants from the site returning into the River Dee when the flood waters recede. | L
Implementing the above measures will significantly reduce the probability and risk of failure from the concrete tanks and significantly reduce the amount of secondary containment. As per CIRIA 736, the above will need to be implemented in conjunction with a good maintenance strategy as mentioned in Box 5.2,Page 60.

## 3.Containment volume-Total vol.
3.1 | Secondary containment volume requirement - Inventory volume (above ground)
| All Tanks | 7446 | m3 | (Inventory volume - above ground below overflow)
| Total volume | 7446 | m3
25% rule (CIRIA 736)
| *25% of all tanks | 1861.5 | m3
| Secondary storage to be provided | 1861.5 | m3
*Note that 10% includes for rainfall and is the minimum allowable storage that can be provided
3.2 | Loss of containment - Time to empty fully
Quick estimation of rate of loss of containment. Modelling will, however, simulate an instantaneous failure of the full volume
Rate of flow from tank:
| Tank volume |  |  | 1861.5 | m3
| Diameter of pipe (d) |  |  | 0.25 | m
| Area |  |  | 0.049087 | m2
| Discharge coefficient (Cd) |  |  | 0.61
| Gravitational acceleration (g) |  |  | 9.81 | m/s2
| Height within tank (H),m | Flow rate (Q) m3/s | Diameter of Tank(m) | Volume in tank (m3) - above ground | % volume lost | Time to drop in level (min) | Time to empty (cumulative) - min
| 12 | 0.45945 | 15.02 | 2126.2337 | -14.22% |  | 0
| 11 | 0.43989 | 15.02 | 1949.0475 | -4.703% | 6.4274 | 6.4274 |  | Height of tank taken from largest tank (digester) within the site
| 10 | 0.41942 | 15.02 | 1771.8614 | 4.815% | 6.7133 | 13.1407
| 9 | 0.3979 | 15.02 | 1594.6753 | 14.33% | 7.0409 | 20.1816
| 8.5 | 0.38669 | 15.02 | 1506.0822 | 19.09% | 3.7109 | 23.8925
| 8 | 0.37514 | 15.02 | 1417.4891 | 23.85% | 3.8185 | 27.711
| 7.5 | 0.36323 | 15.02 | 1328.896 | 28.61% | 3.936 | 31.647
| 7 | 0.35091 | 15.02 | 1240.303 | 33.37% | 4.0651 | 35.712
| 6.5 | 0.33815 | 15.02 | 1151.7099 | 38.13% | 4.2078 | 39.9198
| 6 | 0.32488 | 15.02 | 1063.1168 | 42.89% | 4.3666 | 44.2864
| 5.5 | 0.31105 | 15.02 | 974.5238 | 47.65% | 4.5449 | 48.8313
| 5 | 0.29657 | 15.02 | 885.9307 | 52.41% | 4.747 | 53.5783
| 4.5 | 0.28136 | 15.02 | 797.3376 | 57.17% | 4.9787 | 58.557
| 4 | 0.26526 | 15.02 | 708.7446 | 61.93% | 5.248 | 63.8049
| 3.5 | 0.24813 | 15.02 | 620.1515 | 66.69% | 5.5663 | 69.3713
| 3 | 0.22973 | 15.02 | 531.5584 | 71.44% | 5.9507 | 75.3219
| 2.5 | 0.20971 | 15.02 | 442.9653 | 76.2% | 6.4274 | 81.7494
| 2 | 0.18757 | 15.02 | 354.3723 | 80.96% | 7.0409 | 88.7903
| 1.5 | 0.16244 | 15.02 | 265.7792 | 85.72% | 7.872 | 96.6623
| 1 | 0.13263 | 15.02 | 177.1861 | 90.48% | 9.0898 | 105.7521
| 0.5 | 0.093785 | 15.02 | 88.5931 | 95.24% | 11.1327 | 116.8847
| 0 | 0 | 15.02 | 0 | 100% | 15.744 | 132.6287 | Minutes to empty to ground level

## 4.Current asset evaluation
4.1 | Current Asset Evaluation | Digester
| Description | Imported and indigenous sludge is pumped for the thickener tank to the digesters. Sludge enters the tanks indirectly through the heatamix units. There are 2 heatamix mixers per digester. Gas is extracted at the top of the digester.
| Number of tanks | 2
| Volume of tank | 1705m3 (approximately) - total volume for each tank 105m3 - above ground (volume above overflow) 1420m3 - above ground (volume below overflow) 180m3 - below ground As per CIRIA 736, if there is an overflow fitted, the overflow level should be taken as the maximum level within the tank and not the brim of the tank.
| Material of tank | Concrete
| Above/below ground? | Above ground with a slight portion below ground
| Pipe material | All connecting pipework is thick-walled stainless steel – some above ground and some below ground. Replacement in 2018
| Drainage for zone | Road to the south drains to gullies connected to 2 soakaways next to the old gas holder - infiltrates into the ground
| Year of construction | 1980 original drawings - roof refurbished and some of the pipework in 2018
| Surrounding area | Surrounding external area is stone - permeable
| Is asset fit for purpose? | The tanks were originally designed and constructed to hold digestate sludge and has been operating with no notable concerns. Tank has not undergone a change of use
| Condition of the tank Any tank failures - cracks, flaking, corrosion, overflows, overfilling? | Roof lifted in the past - not after roof refurbishment in 2018 Crack above pump - no structural concern (weeping crack) Foaming not been an issue - no incidents reported by operations yet
| Condition of pipework Pipe leaks, corrosion? | No visible issues/leaks reported by operational staff Additional stainless steel pipes were installed in 2018
| Protection of assets - bollards? | No vehicle impact protection - plans to add a fence around the area
| Control/monitoring/alarming measures in place? | Flow controlled to digesters - level and temperature in digester, failure of recirculation or mixing pumps. The level within the tanks are monitored by ultrasonic level sensors, but not linked to Scada or alarmed.
| Secondary containment provided? | None
| Secondary containment condition? | N/A

## 5.Containment type-Total vol.
5.1 | Containment to be provided
Based on a Medium site risk rating for the zone, Class 3 containment is required. Bunds, as shown below, or concrete walls will be used
Typical Bund section view
Typical reinforced concrete wall section view
5.2 | Catastrophic failure
Catastrophic failure assumes a containment boundary to contain the 25% of the total above ground volume of all sludge containing assets.
Location of Sludge Treatment Units
Suitability of containment to be provided
| Type |  | Applicability
| Reinforced concrete/masonry flooring and bund |  | Due to relatively large volume from loss of containment, use of a masonry/concrete bund is generally not appropriate for local containment in this scenario. Due to the limited space available around the area, the use of masonry/concrete bunds is however applicable
| Earth banked basins, bunds and flooring |  | Soil within site is of permeable nature - Clay or impermeable soil type not plentiful Potential for stabilised soil (lime and cement used to make it impermeable) for bund construction. Area of which bunding can be provided is however limited - assuming for example a bund height of 300mm, crest width of 100m, side slopes of 1:3 - a base width of the bund of at least 2000mm is required. Dependant on area required and nature of surrounding area, might be applicable Not applicable within the digester area.
| Containment tank |  | Nature of catastrophic failure and type of primary containment makes use of a containment tank not appropriate
5.3 | Catastrophic failure in existing situation (Do Nothing) - Visualisation
Figure 5.3.1 Visualisation of Do Nothing Option
Figure 5.3.2 Visualisation of Do Nothing Option - With Existing Secondary Containment Option
5.4 | Type of containment to be provided
Proposed Option: Local containment
Volume is proposed to be contained within the site and will be constructed within the treatment works site boundary. Where currently permeable (stone and grass), to be made impermeable with either converting this to a concrete surface or via lining. Drainage arrangment to be updated to incorporate the rainfall from the bunded site to the drainage pumping station constructed during the previos phase, ensureing that in case of failure, sludge cannont escape the boundary. Daily operational inspection to ensure any rainfall runoff within the bund is removed. As per the new modelling result, new walls are needed to be constructed ranging up to 1.4 m with the addition of freeboard. During previous phase of the project, some containment walls were constructed, the height of which at certain locations should be to be increased as per the modelling result. This would limit flow throughout the entire site and contain it to the site boundary. To enable access into the contained area, speed humps of 100mm are are porvided toward the west side and a 400mm high ramp is porvided towards the south side for easy vehicular access. Details about the length and a slope of the ramp is to be decided during detailed design The proposed wall heights are sufficient to contain up to 1861.5m3, which is the volume modelled using 25% of the total storage capacity within the bunded area but excluding any freeboard. Refer B16383-123532-ZZ-XX-RP-YB-HY0139 - Queensferry containment risk assessment for details of the containment volume and selection of the containment boundary. This option protects the entire site from failure into the nearby river Dee and grassed areas from all the tanks listed in the permit.
Figure 5.4.1. Proposed Option
Figure 5.4.2. Visualisation of Proposed Option
| Advantages | Sludge is kept on-site and out of the identified receptors outside the site boundary. Spills from any tanks registered in the IED permit are contained in case of failure. No requirement of floodgates for access into the contained areas as the necessary containment is obtained either by providing sleeping policeman or ramps
| Disadvantages | Large area needs to be made to hardstanding.