Dale Wastewater Treatment Works (BP0064001)

Membrane Filtration

MAINTENANCE, MONITORING, RECORDING AND REPORTING

A maintenance programme, including the method and frequency of cleaning and replacement of membrane filters, on-line turbidity meters, and flow meters will be established within the DCWW management system, the operations and records will be made available to Natural Resources Wales (NRW) on request.

DCWW will retain records of the maintenance undertaken (both planned and unplanned). Copies of these records shall be held within DCWW management system and made available for inspection by NRW officers at all reasonable times.

Process Monitoring and Reporting

Continuous recorders, with on-site visual display from which readings may be readily obtained, shall be provided and maintained by DCWW enabling:
(i) the instantaneous effluent flow rate to be recorded at hourly, or more frequent intervals to be agreed in writing with NRW;
(ii) the instantaneous effluent turbidity after membrane filtration to be measured and recorded at hourly, or more frequent intervals to be agreed in writing with NRW;
(iii) copies of the records will be retained by DCWW for a minimum of 2 years and be held within DCWW management system and made available for inspection by NRW officers at all reasonable times;

Records of Maintenance and Incidents of failure

Records of the maintenance undertaken, including any details and an explanation of the circumstances where the agreed maintenance programme where not met will be made available to NRW on request.

On request, DCWW will supply NRW, a written report detailing all occurrences when at any time:
(i) there were any failures of any measurement system used to control the membrane filtration system;
(ii) the external power supply to the membrane filtration system was interrupted;
(iii) where effluent turbidity exceeded 30 NTU (nephelometric turbidity units);
(iv) A discharge of sewage effluent was made which had not been subjected to treatment by membrane filtration as specified in table S1.1 of this permit;
(v) The report shall detail the reasons why the situation occurred, and the actions taken by the DCWW. The report shall include an assessment of what measures can be adopted in the future to minimise such occurrences.

TELEMETRY

A telemetry alarm system connected to a 24-hour manned station will be provided and maintained by DCWW to provide a warning in the event that:
(a) the external power supply to the treatment system has been interrupted;
(b) there has been a mechanical or control system breakdown;
(c) the effluent turbidity exceeds 30 NTU (nephelometric turbidity units).
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