[image: image2.png]Cyfoeth
Naturiol
Cymru

Natural
Resources
Wales





Notice of variation and consolidation with introductory note

The Environmental Permitting (England & Wales) Regulations 2016
St John’s College Limited
Package treatment plant and infiltration system serving
St John’s College Sports Pavilion and Playing Fields

Began Road

St Mellons

Cardiff

CF3 6XL

Variation application number

EPR/DP3922XG/V005
Permit number
EPR/DP3922XG
Package treatment plant and infiltration 

system serving St John‘s College Sports 

Pavilion and Playing Fields
Permit number EPR/DP3922XG
Introductory note

This introductory note does not form a part of the notice.

The following notice gives notice of the variation and consolidation of an environmental permit.
The schedules specify the changes made to the permit.
Following a site inspection in 2025, it was noted that the discharge point on the permit issued in 2010 is incorrect. The Operator initiated variation is to amend the permit from a discharge to surface water to a discharge to groundwater via an infiltration system. The suspended solids limit has been removed because the discharge is no longer going to surface water. 
The status log of a permit sets out the permitting history, including any changes to the permit reference number.  
	Status log of the permit

	Description
	Date
	Comments

	Application received

EPR/DP3922XG/A001
	Duly made 30/06/2010
	Application to discharge secondary treated sewage effluent

	Permit determined 

EPR/DP3922XG
	29/10/2010
	Permit issued to St John’s College Limited

	Application EPR/DP3922XG /V002

(Admin variation)
	Duly made

25/04/2012
	Application to vary the start date

	Variation determined EPR/DP3922XG
	27/04/2012
	Varied permit issued

	Application EPR/DP3922XG /V003
(Admin variation)
	Duly made

14/06/2013
	Application to vary the start date

	Variation determined

EPR/DP3922XG 
	12/07/2013
	Varied permit issued

	Application EPR/DP3922XG /V004
(Admin variation)
	Duly made

26/06/2014
	Application to vary the start date

	Variation determined

EPR/DP3922XG 
	10/07/2014
	Varied permit issued

	Application received

PAN-028618
	Duly made

02/04/2025
	Application to vary the permit from  discharge to surface water to groundwater

	Variation determined

EPR/DP3922XG/V005
	30/06/2025
	Varied permit issued


End of introductory note

	Notice of variation and consolidation 


The Environmental Permitting (England and Wales) Regulations 2016
The Natural Resources Body for Wales (“Natural Resources Wales”) in exercise of its powers under regulation 20 of the Environmental Permitting (England and Wales) Regulations 2016 varies and consolidates
permit number

EPR/DP3922XG
issued to:

St John’s College Limited (“the operator”)

whose registered office is
College Green
Newport Road

Old St Mellons

Cardiff

CF3 5YX

company registration number 02114449
to operate a regulated facility at
St John’s College Sports Pavilion
Began Road Playing Fields

Old St Mellons

Cardiff

CF3 6XL

to the extent set out in the schedules.
The notice shall take effect from 30 June 2025
	Name
	Date

	Emma Jones
	30/06/2025


Authorised on behalf of Natural Resources Wales
Schedule 1 

Only conditions Table 3.1, 2.3.1, Table 1.1, Table 3.1, Tables 3.2 and 3.3 and Schedule 7 have been varied by the consolidated permit ERP/DP3922XG:
- The following conditions were varied as a result of an Natural Resources Wales initiated variation:

Table 3.1 – Suspended solids limit has been removed.  
- The following conditions were varied as a result of the application made by the operator:

2.3.1 Operating Techniques
Table 1.1 Activities
Table 3.1 Emission Point Ref and Location
Tables 3.2 and 3.3 – Discharge points and Monitoring Points
Schedule 7 - Site Plan

Schedule 2 – consolidated permit

Consolidated permit issued as a separate document. 
	Permit


The Environmental Permitting (England and Wales) Regulations 2016
Permit number 

EPR/DP3922XG
This is the consolidated permit referred to in the variation and consolidation notice for application PAN-028618 authorising, 
St John’s College Limited (“the operator”),

whose registered office is 

College Green
Newport Road

Old St Mellons

Cardiff

CF3 5YX

company registration number 02114449
to operate a groundwater activity at

St John’s College Sports Pavilion

Began Road Playing Fields

Old St Mellons

Cardiff

CF3 6XL

to the extent authorised by and subject to the conditions of this permit.

	Name
	Date

	Emma Jones
	30/06/2025


Authorised on behalf of Natural Resources Wales
Conditions 

1 Management
1.1 General management

1.1.1 The operator shall manage and operate the activities:

(a) in accordance with a written management system that identifies and minimises risks of pollution, including those arising from operations, maintenance, accidents, incidents, non-conformances and those drawn to the attention of the operator as a result of complaints; and

(b) using sufficient competent persons and resources.

1.1.2 Records demonstrating compliance with condition 1.1.1 shall be maintained. 

1.1.3 Any person having duties that are or may be affected by the matters set out in this permit shall have convenient access to a copy of it kept at or near the place where those duties are carried out.

2
Operations
2.1
Permitted activities

2.1.1
The operator is only authorised to carry out the activities specified in schedule 1 table S1.1 (the “activities”). 

2.2
The site 
2.2.1
The activities shall not extend beyond the site, being the land shown edged in green and the discharge shall be made at the point marked on the site plan at schedule 7 to this permit and as listed in table S3.2 (discharge points). 

2.3
Operating techniques

2.3.1
The infiltration system specified in table S1.1 shall be constructed to comply with the following:

(a) no part of the infiltration system constructed shall be more than 2 metres below ground level;

(b) no part of the infiltration system shall be less than 1.2 metres above the highest predicted annual groundwater level;
(c) the infiltration system shall not connect to any land drainage system;

(d) the infiltration system shall not be situated within 10 metres of any watercourse (including any ditch that runs dry for part of the year), or any other surface water;
(e) the infiltration system shall not be situated within 50 metres of a well or borehole used for water supply.

.
3
Emissions and monitoring
3.1
Emissions to water, air or land
3.1.1
There shall be no point source emissions to water, air or land except from the sources and emission points listed in schedule 3 tables S3.1, S3.2 and S3.3.

3.1.2
    The limits given in schedule 3 shall not be exceeded.

3.2 Emissions of substances not controlled by emission limits

3.2.1
For the activity referenced in schedule 1, table S1.1 the operator shall take appropriate measures as far as is reasonably practicable:

1 to prevent the input of hazardous substances to groundwater; and
1 where a non-hazardous pollutant is not controlled by an emission limit, to limit the input of such non-hazardous pollutants to groundwater so as to ensure that inputs do not cause pollution of groundwater.
3.3
Monitoring 

3.3.1
Permanent means of access shall be provided to enable sampling/monitoring to be carried out in relation to the emission points specified in schedule 3 tables S3.1, S3.2 and S3.3 unless otherwise agreed in writing by Natural Resources Wales.

4
Information

4.1
Records
4.1.1 All records required to be made by this permit shall:

(a) be legible;

(b) be made as soon as reasonably practicable;

(c) if amended, be amended in such a way that the original and any subsequent amendments remain legible, or are capable of retrieval; and

(d) be retained, unless otherwise agreed in writing by Natural Resources Wales, for at least 6 years from the date when the records were made.
4.1.2
The operator shall keep on site all records, plans and the management system required to be maintained by this permit, unless otherwise agreed in writing by Natural Resources Wales. 

4.2
Reporting
4.2.1
The operator shall send all reports and notifications required by the permit to Natural Resources Wales using the contact details supplied in writing by Natural Resources Wales.

4.3
Notifications
4.3.1
    Natural Resources Wales shall be notified without delay following the detection of:

(a) any malfunction, breakdown or failure of equipment or techniques, accident, or  emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution;

(b) the breach of a limit specified in the permit; or 

(c) any significant adverse environmental effects.  

(d)
any emergency discharge that has occurred.  
4.3.2
Any information provided under condition 4.3.1 shall be confirmed by sending the information listed in schedule 5 to this permit within the time period specified in that schedule.
4.3.3
Where Natural Resources Wales has requested in writing that it shall be notified when the operator is to undertake monitoring and/or spot sampling, the operator shall inform Natural Resources Wales when the relevant monitoring and/or spot sampling is to take place. The operator shall provide this information to Natural Resources Wales at least 14 days before the date the monitoring is to be undertaken.
4.3.4
Natural Resources Wales shall be notified within 14 days of the occurrence of the following matters, except where such disclosure is prohibited by Stock Exchange rules: 

Where the operator is a registered company:
(a) any change in the operator’s trading name, registered name or registered office address; and

(b)
any steps taken with a view to the operator going into administration, entering into a company voluntary arrangement or being wound up.

Where the operator is a corporate body other than a registered company:

(a)         any change in the operator’s name or address; and

(b) any steps taken with a view to the dissolution of the operator.

4.3.5
Where the operator proposes to make a change in the nature or functioning, or an extension of the activities, which may have consequences for the environment and the change is not otherwise the subject of an application for approval under the Regulations or this permit:

(a) Natural Resources Wales shall be notified at least 14 days before making the change; and

(b)
        the notification shall contain a description of the proposed change in operation.
4.4
Interpretation
4.4.1
In this permit the expressions listed in schedule 6 shall have the meaning given in that schedule.

4.4.2
In this permit references to reports and notifications mean written reports and notifications, except where reference is made to notification being made “without delay”, in which case it may be provided by telephone. 

Schedule 1 – Operations

	Table S1.1 Activities

	Description of activity
	Limits of specified activity

	Groundwater activity: discharge into land of secondary treated sewage effluent
	Via an infiltration system centred on ST 22540 83153.


Schedule 2 - Waste types, raw materials and fuels

Wastes are not accepted as part of the permitted activities and there are no restrictions on raw materials or fuels under this schedule.

 Schedule 3 – Emissions and monitoring

	Table S3.1 Point Source emissions to water (other than sewer) and land – emission limits and monitoring requirements

	Emission point ref. & location
	Parameter  
	Limit (incl. unit)
	Reference 

Period
	Monitoring frequency
	Compliance statistic

	Outlet 1 on site plan in schedule 7 outflow from sewage treatment plant prior to discharge into infiltration system.
	Maximum daily flow
	8.2 m3/day
	Total daily volume
	N/A
	Maximum

	
	Ammoniacal nitrogen (as N)
	30 mg/l
	Instantaneous (spot sample)
	N/A
	Maximum 

	
	ATU-BOD as O2
	30 mg/l
	Instantaneous (spot sample)
	N/A
	Maximum

	
	Visible oil or grease
	No significant trace present
	Instantaneous (spot sample)
	N/A
	No significant trace


	Table S3.2 Discharge points

	Effluent Name
	Discharge Point
	Discharge point NGR
	Receiving Environment



	Secondary treated sewage effluent 
	Outlet 1
	ST 22547 83157
	Groundwater via an infiltration system


	Table S3.3 Monitoring points

	Effluent and discharge point
	Monitoring type
	Monitoring point NGR
	Monitoring point reference

	Secondary treated sewage effluent via outlet 1
	Effluent sampling
	ST 22547 83157
	Outlet 1


Schedule 4 - Reporting

There is no reporting under this schedule.

Schedule 5 - Notification 
These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	EPR-DP3922XG

	Name of operator
	

	Location of Facility
	St John’s College Sports Pavilion and Playing Fields, Began Road, St Mellons, Cardiff CF3 6XL

	Time and date of the detection 
	


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of  release of substances
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	

	Parameter(s)
	

	Limit
	

	Measured value and uncertainty
	

	Date and time of monitoring
	

	Measures taken, or intended to be taken, to stop the emission
	


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	


	Name*
	

	Post
	

	Signature
	

	Date
	


* authorised to sign on behalf of the operator
Schedule 6 - Interpretation 

“accident” means an accident that may result in pollution.

“annually” means once every year.
“application” means the application for this permit, together with any additional information supplied by the operator as part of the application and any response to a notice served under Schedule 5 to the EP Regulations.
“ATU-BOD as O2” means the biochemical oxygen demand (measured after 5 days at 20o C with nitrification suppressed by the addition of allylthiourea).

“emissions to land” includes emissions to groundwater.

“EP Regulations” means The Environmental Permitting (England and Wales) Regulations SI 2016 No.1154 and words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.

“emissions of substances not controlled by emission limits” means emissions of substances to air, water or land from the activities, either from the emission points specified in schedule 3 or from other localised or diffuse sources, which are not controlled by an emission limit.
“groundwater” means all water, which is below the surface of the ground in the saturation zone and in direct contact with the ground or subsoil.
“Natural Resources Wales” means the Natural Resources Body for Wales established by article 3 of the Natural Resources Body for Wales (Establishment) Order 2012. The Natural Resources Body for Wales (Functions) Order 2013 transferred the relevant functions of the Countryside Council for Wales, and functions of the Environment Agency and the Forestry Commission in Wales to the Natural Resources Body for Wales.
“quarter” means a calendar year quarter commencing on 1 January, 1 April, 1 July or 1 October.
“year” means calendar year ending 31 December.

Schedule 7 - Site plan
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© Crown Copyright and database right 2025. Ordnance Survey licence number 100019741.
END OF PERMIT
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