Pumping Station Emergency Discharge Key Protection Measures

	Site name:
	Afan WwTW Emergency Overflow

	Permit Number and Activity Reference:
	BP0284701

	Version number and Date
	V2 July 2025

	
	

	Pumps:
	Duty pump(s) installed and maintained in working order:
	Yes

	
	Standby pump(s) installed and maintained in working order :
	Yes

	
	Automatic standby pump activation on duty pump failures other than power failure:
	Yes

	
	Automatic pump reactivation as soon as is practicable  when power restored after power failure:
	Yes

	
	Over pumping facility installed and maintained for use if the installed pumps are inoperative:
	No

	
	Tanker access provided and maintained at an appropriate location to enable removal of sewage by tanker when necessary:
	Yes

	
	
	
	

	Maintained 24 hour response telemetry alarm system to; 
	Notify Operator:
	Provided

	
	Failure or breakdown of the pumping station
	Yes

	
	Overflow operating 
	Yes



	Alarm response
	Response:
Take all reasonable remedial measures to return the pumping station to normal operation.  
	Yes

	
	Response time:
As soon as reasonably practicable after receipt of warning of failure or breakdown of the pumping station
	Yes

	
	

	Standby power provision:
	Mobile generator point. Install and operate a mobile generator as soon as is reasonably practicable in the event of an electrical failure
	Yes

	
	Permanent standby generator installed and maintained in good working order and activated as soon as reasonably practicable in the event of an electrical power failure. 
	No

	
	Duplicate power supply provided, and activated as soon as reasonably practicable in the event of an electrical  power failure
	Yes

	
	

	Emergency storage capacity Hours @ DWF*: 
	Storage capacity, equivalent to a total of at least x hours of the dry weather flow* (“DWF*”), shall be provided above the normal top operating level in dry weather and below the level of the overflow.
Must complete where emergency provisions are new, reassessed, or storage was previously specified in hrs@DWF. Optional elsewhere. X must be agreed with Agency and will equate to the emergency storage capacity (m3) below divided by the design DWF limit (PG+I+E) (m3/day) below. And is expressed in (hours)
	4200m equivalent to at least 1.9hrs of DWF

	* For compliance purposes Dry Weather Flow shall mean the average daily flow entering the pumping station during seven consecutive days without rain (excluding a period which includes public holidays) following seven days during which the rainfall did not exceed 0.25 millimetres on any one day. The DWF figure you enter should be based on your estimate of PG+I+E at your chosen design horizon.


	Design dry weather flow limit
	The figure proposed here should be based on the projected PG + I + E at your proposed design  horizon:
Only complete where storage is specified above in hrs@DWF*.
	401 l/s

	Emergency storage capacity m3
	Minimum storage volume provided above the normal top operating level in dry weather and below the level of the overflow
Complete in all cases
	4200



	Screening:
	Screen fitted
	Y

	
	Screen type
	Mesh

	
	Screen aperture size
	6mm

	Any other key protection measures (e.g. enhanced target response times, links and dependencies to other pumping stations such as pump inhibits and tankering at upstream pumping stations in an emergency):
	
N/A







