Schedule 5 - Notification                            TIR0293 19/06/2025

Part A 
	Permit Number
	VP3935AT

	Name of Operator
	Enovert South Ltd

	Location of Installation
	Tir John Landfill, Wern Terrace, Off Fabian Way, Swansea, SA1 8PA

	Time and date of the detection 
	May 2025

	(b) Notification requirements for the breach of a limit (within 24 hours unless otherwise agreed)

	Emission point reference/ source
	Phase 2 LEW Leachate Wells
Leachate Head above Cell Base
>1m
See Table 1 Below

	Parameter(s)
	

	Limit
	

	Measured value and uncertainty
	

	Date and time of monitoring
	

	Measures taken, or intended to be taken, to stop the emission
	Leachate remains contained within the engineered containment system, so no emission from the site is occurring.


Part B to be supplied as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	Leachate removal to sewer is ongoing. 

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	Landfill capping works are almost complete, and we may experience new fluctuations across leachate levels as the site settles. It is unlikely that all the dipped levels are representative of the actual leachate levels in the waste mass. It is likely that as the waste ages and compresses, the pore spaces are reduced, and liquid is effectively squeezed out into the wells.
Pumping, capping and drainage methods have impacted average leachate heads across the site, which appear to be following a downward trend year on year.

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	The elevated levels in wells LEW15a and LEW16 are due to well or pump clogging issues. Solutions have been under discussion within Enovert and with NRW. Initial dosing with bleach failed to break up the blockage, we have trialled dosing material with citric acid which does soften it to some extent, but the process is extremely slow and not practical for site application. We continue to use physical methods to maximise extraction from Cell 16. The substance will be sampled for further laboratory analysis and testing of treatment methods. We have commissioned consultants to support us with this work.

	The dates of any unauthorised emissions from the installation in the preceding 24 months.
	See previous notifications.


	Name*
	Elizabeth Forrest

	Post
	Environmental Data Analyst

	Date
	19/06/2025


[bookmark: _Int_iiKeGdxg]* authorised to sign on behalf of Enovert South Ltd





	Sample Point
	Date
	Leachate Head (m)
	Comment

	LEW07
	14/05/2025
	1.30
	

	LEW12a
	14/05/2025
	1.07
	

	LEW15a
	14/05/2025
	
	Affected by solidifying substance

	LEW16
	14/05/2025
	
	Affected by solidifying substance

	LEW21
	14/05/2025
	3.49
	

	LEW22
	14/05/2025
	3.01
	

	LEW23
	14/05/2025
	3.32
	

	LEW24
	14/05/2025
	3.41
	

	LEW25
	14/05/2025
	2.18
	

	LEW26
	14/05/2025
	1.71
	

	LEW28
	14/05/2025
	4.54
	

	LEW29
	14/05/2025
	7.22
	

	LEW30
	14/05/2025
	3.68
	

	LEW31
	14/05/2025
	4.79
	

	LEW32
	14/05/2025
	3.24
	


Table 1: Breach of Compliance Limit for Leachate Boreholes Phase 2 area May 2025


