While we appreciate that there has been a permit for waste activities on this site previously, the PAN-025329 application has been assessed solely on its own merit, against our current guidance and duly making requirements.

The following assessments and management plans have not been completed, but are required by our guidance:

- Noise

A noise impact assessment and noise management plan are required for the site and proposed activities. Due to the following:

- There are 3 residential receptors within 170 meters of the site, and a builder’s merchants on the northern boundary

- External activities are crushing and/or screening of aggregates and soils and the storage in stockpiles or skips of non-hazardous and inert wastes, covered/containerised storage of hazardous and quarantined wastes, and for empty skip storage.

- The activity is occurring in a rural area.

Guidance on Noise Impact Assessments and Noise Management Plans can be found on our website- Natural Resources Wales / Horizontal guidance

- Dust

The Dust Management Plan guidance states that you must provide a dust management plan if you are applying for a bespoke permit for any of the activities listed below and your site is in either of the locations listed below:

- Relevant proposed activities include keeping or treating (or both) aggregates, soils, ashes or similar materials, keeping or treating (or both) wood, keeping or treating (or both) household, commercial or industrial waste in a waste transfer station, keeping or treating (or both) scrap metal, receiving, processing or producing fine or dusty materials

- Within 500 meters of residential (and recreational) receptors

As such a Dust Management Plan is required. The guidance states what information should be in a Dust Management Plan.

The following information needs to be provided, otherwise the activities proposed cannot be considered a waste activities, and an installation application must be made instead:

- Industrial Emissions Directive (IED) Activity

Several activities are proposed that could fall under the Industrial Emissions Directive and could therefore be an installation rather than a waste activity. These activities are (1) Pre-treatment of waste for incineration and co-incineration, (2) Storage of hazardous waste, and (3) Treatment of slags and ashes.

The application states that the hazardous waste storage capacity is 10 tonnes at any one time (for information, the legal limit is 50 tonnes at any one time).

However, information must be provided on the treatment types and treatment capacities for Pre-treatment of waste for incineration/co-incineration and Treatment of slags and ashes.

Pre-treatment of waste for incineration/co-incineration has been included as the application states that "Baling of combustible wastes to produce fuel for recovery or disposal (determined by the end use)" is to be undertaken. It must be clarified what the on-site treatment capacity is. It must be under the limits below to be considered a waste activity.

Treatment of slags and ashes has been included as wastes consisting of slags and ashes are listed in the application. It must be clarified if slags and ashes are to undergo any treatment other than sorting and bulking up. If the intention to undergo additional treatments, it must also be clarified what the on-site treatment capacity is. It must be under the limits below to be considered a waste activity.

For information, the limits are as follows:

SECTION 5.4 Disposal, recovery or a mix of disposal and recovery of non-hazardous waste

Part A(1)

(a) Disposal of non-hazardous waste with a capacity exceeding 50 tonnes per day —

(iii) pre-treatment waste for incineration or co-incineration;

(iv) treatment of slags and ashes;

(b) Recovery or a mix of recovery and disposal of non-hazardous waste with a capacity exceeding 75 tonnes per—

(ii) pre-treatment of waste for incineration or co-incineration;

(iii) treatment of slags and ashes;

The following information/documents have been provided, but are not complete or follow the guidance:

- 11109 Environmental Management System

The EMS has been reviewed against our guidance; the following should be included:

- Operations- information on procedures to segregate incompatible wastes for example use of appropriate separation distances and or suitable engineering measures.

- Non-compliance- information on how non-compliance will be dealt with including recording, investigating and resolution

- Closure- information on the plans in place to close the site

The EMS may need to be updated following the findings of the NIA, NMP and DEMP, and information following the updates to the other management systems.

- 11109 Environmental Risk Assessment

The Risk assessment has been reviewed; the following amendments need to be made:

- The Noise and vibration section of the Risk Assessment is cut off- the full extent of the text cannot be seen.

- Some areas of the site have hardstanding; however, this is not addressed in relation to the risks to groundwater.

- The closest residential receptor Yet-Y-Gors is given as being approximately 115m southeast from the site boundary; however, our measurements makes this to be 95 meters from the site boundary. These distances need to be reviewed.

The risk assessment may need to be updated following the findings of the NIA, NMP and DEMP, and information following the updates to the other management systems.

- 11109 Fire Prevention and Mitigation Plan

The Fire Prevention and Mitigation Plan (FPMP) has been reviewed against our guidance. The following information is missing and must be included:

Section 5. Fire Prevention and Mitigation Plan contents

- The amount and type of waste received daily and how it is managed.

- The forms of waste (e.g. unprocessed, shredded etc) stored on site

- Minimum separation distances used- no separation distances have been included in the FPMP or drawings/plans

- Clear area around the perimeter

- Fire prevention techniques used, including management of hotspots, self combustion, monitoring, reporting

- Techniques used to minimise fire spreading

Section 6. Common causes of fires and preventative measures

- Build-up of loose combustible waste, dust and fluff not included in Table 6

Section 7. Storage times and self combustion factors

- Wastes at risk of self combustion that are being stored for more than 3 months include Wood Waste, WEEE Waste, Li-ion batteries, Waste Oil, however additional measures to ensure these wastes will not combust have not been included.

Section 8. Managing waste material stacks

- No separation distances have been given in the FPMP

Section 11. Enclosing stacks using bales and walls

- This section of the guidance has not been followed in the FPMP

Section 12. Waste stored within a building

- This section of the guidance has not been followed in the FPMP

Section 13. Waste stored in containers

- This section of the guidance has not been followed in the FPMP

Section 15. Seasonality and waste stack management

- This section of the guidance has not been followed in the FPMP

Section 16. Monitoring and turning of stacks

- This section of the guidance has not been followed in the FPMP

Section 19. Firefighting strategy

- the FPMP does not include information on the suitability of the heavy plant that may be used to move burning waste.

Section 20. Water supplies

- amount of water required for largest stack has not been calculated or given

- a hydrant has been proposed as the sole source of water to fight a fire; however, no information is included to demonstrate the hydrant is suitable

- No alternative sources of water have been proposed.

Section 21. Managing water run-off

- This section of the guidance states that fire water should be prevented from entering into the ground, however this is in fact being proposed in the FPMP, therefore fire water is not being “contained on site”

- FPMP does not include calculations to demonstrate how much water can be contained

- measures to prevent firewater reaching groundwater have not been included

Section 22. Designated quarantine area

- no separation distances for the quarantine area(s) have been given

Section 23. During and after an incident

- the FPMP does not include contingency measures during and after a fire

- the FPMP does not include how the site will be cleared and decontaminated- only the removal of fire waste has been mentioned in Section 11.

Section 24. Reviewing and monitoring your FPMP

- the FPMP does not include when and under what circumstances it will be reviewed.

- 11109 Odour Management Plan

The Odour Management Plan (OMP) has been reviewed against our guidance, and our general requirements for management plans. The following information is missing and must be included:

Site Overview

- operating hours given differ to those given in the EMS and FPMP

- waste codes- only waste types are given (Table 3)

- daily / annual throughput limit- only the amounts of waste stored at any one time given

Site Plan

- All waste storage areas- only building outlines have been shown

- Layout of internal waste storage areas- only building outlines have been shown

- Monitoring points- while Drawing 11109 - 000 - L has "ODOUR ASSESSMENT BOUNDARIES" in the key, but this is not shown on the drawing

Training, Record Keeping and Review of the OMP

Information on:

- how staff will be trained on the OMP

- how appropriate records will be kept (for example of monitoring, complaints)

- how the records of the monitoring and complaints will be reviewed with the aim of improving operations on site

- how regularly and when the entire OMP will be reviewed

- 11109 Technical Ability

The primary competence provided is Medium Risk Operator Competence for Non-Hazardous Waste Treatment and Transfer- issued 02/11/16- expired 02/11/2018.

The continuing competence provided are:

- TSH- Transfer Hazardous waste- issued 11/07/2023- expires 14/07/2025

- TMH- Treatment- Hazardous Waste- issued 12/07/2023- expires 17/07/2025

On reviewing the three activities applied for:

- Hazardous Waste Transfer Station

The required primary competence is HROC4a https://ciwmquals.co.uk/wp-content/uploads/2023/11/CIWM-Purpose-Statement_V3_HROC4.pdf

The required continuing competence is TSH

The primary award cannot be used, but the continuing competence can be used.

- Non-Hazardous HCI Waste Transfer Station with Treatment

The required primary competence is: MROC1 https://ciwmquals.co.uk/wp-content/uploads/2023/11/CIWM-Purpose-Statement_V3_MROC1.pdf

The required continuing competence is TMNH

The primary award can be used, but the continuing competence is not correct.

- Inert and Excavation Waste Transfer Station with Treatment

The required primary competence is: LROC4 https://ciwmquals.co.uk/wp-content/uploads/2023/11/CIWM-Purpose-Statement_V3_LROC4.pdf

The required continuing competence is TMNH

The primary award can be used, but the continuing competence is not correct.

In conclusion the following is required to be obtained:

- primary competence of HROC4a https://ciwmquals.co.uk/wp-content/uploads/2023/11/CIWM-Purpose-Statement_V3_HROC4.pdf

- continuing competence of TMNH

- Application fees

This application was made on 05/04/2024, therefore 2024/25 charging guidance and application fees apply (as of 01/04/2024), however the fees paid were based on the 2023/24 charging guidance and application fees.

The current applicable charges for the application made are as follows:

Base charges:

- New bespoke waste permit- £10,011

- Additional activities (2 x 20% of base charge each)- £4,004.40

Charges for reviewing plans and assessments

- Site of Special Scientific Interest (SSSI) assessment- £306 (SSSI included in application, but fee not paid)

- Noise impact assessment and noise management plan- £2,425 (NIA and NMP not included in application, fee not paid, not included in refund calculation)

- Dust and emissions management plan (DEMP)- £861 (DEMP not included in application, fee not paid, not included in refund calculation)

- Odour management plan- £1,619 (fee paid)

- Fire prevention and mitigation plan (FPMP)- £2,343 (fee paid)

- Discharge to water- £390 (fee paid)

Total: £21,959.40

Please note that £14,191.78 of the fees paid for this application are to be refunded.