Pumping Station Emergency Discharge Key Protection Measures
	Site name:
	Nolton Haven SPS

	Permit Number and Activity Reference:
	EPR/UP3629XK

	Version number and Date
	Version 1, 1st April, 2014

	
	

	Pumps:
	Duty pump(s) installed and maintained in working order:
	Yes duty/assist

	
	Standby pump(s) installed and maintained in working order :
	No Duty/assist configuration

	
	Automatic standby pump activation on duty pump failures other than power failure:
	Assist act as standby

	
	 pump reactivation as soon as is practicable when power restored after power failure:
	

	
	Over pumping facility installed and maintained for use if the installed pumps are inoperative:
	no

	
	Tanker access provided and maintained at an appropriate location to enable removal of sewage by tanker when necessary:
	yes

	
	
	
	

	Maintained 24 hour response telemetry alarm system to; 
	Notify Operator:
	Provided

	
	Failure or breakdown of the pumping station
	yes

	
	Overflow operating 
	Yes (EDM monitor)

	
	
	

	Alarm response
	Response 
	Response time

	
	N/A
	N/A

	
	

	Standby power provision:
	Mobile generator point. Install and operate a mobile generator as soon as is reasonably practicable in the event of an electrical failure
	Plug in socket for mobile generator connection

	
	Permanent standby generator installed and maintained in good working order and activated automatically in the event of an electrical power failure. 
	No

	
	Duplicate power supply provided,  maintained and activated <automatically/as soon as reasonably practicable>(delete as appropriate) in the event of an electrical  power failure
	No

	
	

	Emergency storage capacity: 
	Storage capacity, equivalent to a total of at least x hours of the dry weather flow* (“DWF*”), shall be provided above the normal top operating level in dry weather and below the level of the overflow.
	2.2 hours

	Basis of hours @ DWF* emergency storage provision
	DWF* limit (The figure proposed should normally allow for growth before a permit review is needed):
	8.7 m3/day)

	
	Minimum storage volume provided above the normal top operating level in dry weather and below the level of the overflow
	Volume (m3)
N/A

	* For the purpose of this condition Dry Weather Flow shall mean the average daily flow entering the pumping station during seven consecutive days without rain (excluding a period which includes public holidays) following seven days during which the rainfall did not exceed 0.25 millimetres on any one day.

	Screening:
	Screen fitted
	Yes

	
	Screen type
	static

	
	Screen aperture size
	6mm 2d

	Any other key protection measures (e.g. enhanced target response times, links and dependencies to other pumping stations such as pump inhibits and tankering at upstream pumping stations in an emergency):
	



