| Permit Number: | BP0366401 (PAN-007498) |
| --- | --- |
| Applicant name: | Dwr Cymru Cyfyngedig |
| Site Address: | Llys y Fran Dam STW |
| Discharge Point NGR: | SN 03886 24216 |
| Respond by date: | 19/11/2019 (10 working days) |
| Permitting Officer: | Elliot Burge |

Brief Description of proposal:

The application is to vary the permit to amend the discharge point NGR to SN 03886 24216 temporarily (for 6 months) whilst the new treatment works serving the visitor centre is constructed. The total daily discharge volume will be 9.9m3/day DWF and there is no associated storm discharge as the treatment work deals with foul flows only. Whilst the construction is taking place DCWW will ensure that the current limits on the permit (20mg/l ammonia, 40mg/l BOD and 60mg/l suspended solids) are met throughout the duration by installing an inlet screen, settlement chamber, MBBR Bioreactor and rotating biological contactor plant.

The temporary discharge point is approximately 100m away from the current permitted discharge point, the current permit allows the works to discharge directly to the Afon Syfynwy at SN 03787 24195, the temporary discharge point will be to a small tributary which goes into the Afon Syfynwy. The tributary looks quite insignificant on MyMap, are we satisfied this tributary will have enough flow to receive the discharge?

Once the 6 month period has finished the permit will revert to the current permitted discharge point.

Habitats Screening Report – Designations or protected species/habitats:

The risk screening report can be found on the DMS here.

A SAC, SSSI, Salmon and Trout have been picked up in the report. An HRA, Appendix 4 will be completed and consulted on. Please could a Fishery Officer also make a comment?

Risk Assessment Results (modelling or L1 Risk Assessment):

No new modelling has been undertaken due to the proximity to the current discharge point, the current permit limits will remain (20mg/l ammonia, 40mg/l BOD and 60mg/l suspended solids) if the variation is to be granted.

Miscellaneous:

N/A

NRM Responses:

Environment Management comments:

No adverse comments from a WQ perspective

Officers name: Rod Thomas
Date:

Biodiversity comments:

Officers name:
Date:

Fisheries comments:

Officers name:
Date:

Conservation/Ecology Comments:

Officers name:
Date:

Internal Consultation Responses from other NRW Teams:

Water Quality Planning:

N/A

Officers name:

Date:

Geoscience Response:

N/A

Officers name:
Date:

Flood Risk Management:

N/A

Officers name:
Date:

| External Consultations sent to: | Yes/No |
| --- | --- |
| National Parks |  |
| Water Company regarding Drinking Water Protected Zone / SPZ1 |  |
| Environmental Heath |  |

Any Permitting Responses:

Date: