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Notice of variation and consolidation with introductory note
The Environmental Permitting (England & Wales) Regulations 2016

Dŵr Cymru Cyfyngedig

St. Asaph Wastewater Treatment Works 
Opposite Holiday Park
St. Asaph
Denbighshire
LL17 0HY


Variation number
PAN-020325
Permit number
CM0078101




St. Asaph Wastewater Treatment Works
Permit number CM0078101
Introductory note
This introductory note does not form a part of the notice.

The following notice gives notice of the variation and consolidation of environmental permit CM0078101.

This permit variation and consolidation is to reflect asset improvements that have been agreed between Natural Resources Wales and Dŵr Cymru Cyfyngedig as part of the National Environment Programme. This permit requires the operator to install overflow operation monitoring into storm storage, and MCERTS flow monitoring to record flow passed forward. Compliance assessment against flow passed forward and overflow operation into storm storage will be carried out for the first full calendar year after both monitors have been installed. 

The schedules specify the changes made to the permit.

The status log of a permit sets out the permitting history, including any changes to the permit reference number. It is not backdated before 6th April 2010.

	Status log

	Description
	Date
	Comments

	Regulator initiated variation CM0078101/V001 
	06/04/2011
	Removal of AMP5 UV and telemetry conditions.

	Variation determined
	12/12/2011
	Varied permit issued

	Application CM0078101/V002 
(variation and consolidation)
	Duly Made
17/09/2014
	Application to vary the permit to include seasonal UV conditions.

	Variation determined CM0078101
	29/04/2016
	Varied and consolidated permit issued in modern condition format.

	Application
PAN-010750 
	Duly Made
19/06/2020
	Varied application to include AMP7 Operating Technique.

	Variation determined CM0078101
	08/09/2020
	Varied permit issued.

	Regulator-initiated variation PAN-020325
	22/09/2025
	Variation of permit initiated under PR19 review programme to incorporate improvements to be delivered under AMP7.

	Variation determined CM0078101 
	09/10/2025
	Varied and consolidated permit issued to Dŵr Cymru Cyfyngedig.


End of introductory note.
	Notice of variation and consolidation 


The Environmental Permitting (England and Wales) Regulations 2016

[bookmark: _Hlt13295849][bookmark: OperatorName2]The Natural Resources Body for Wales (“Natural Resources Wales”) in exercise of its powers under regulation 20 of the Environmental Permitting (England and Wales) Regulations 2016 varies and consolidates

permit number
CM0078101

issued to
Dŵr Cymru Cyfyngedig (“the operator”)

whose registered office is
Linea
Fortran Road
St Mellons
Cardiff
CF3 0LT

company registration number 02366777

to operate a water discharge activity at
St. Asaph Wastewater Treatment Works
Opposite Holiday Park
St. Asaph
Denbighshire
LL17 0HY

to the extent set out in the schedules.

The notice shall take effect from 09/10/2025

	Name
	Date

	Joanne Fitton
	09/10/2025


Authorised on behalf of Natural Resources Wales.

Schedule 1 
The following conditions were varied as a result of a Natural Resources Wales initiated variation:
2.4.1, 3.1.6, 3.3.5 (b), 3.3.9, 3.3.11, 3.3.12, 3.3.13, 4.3.6

Schedule 2 – consolidated permit
Consolidated permit issued as a separate document. 
Variation and consolidation
number: PAN-020325	Page i
	
Permit


The Environmental Permitting (England and Wales) Regulations 2016

Permit number 
CM0078101
This is the consolidated permit referred to in the variation and consolidation notice for variation PAN-020325 authorising

Dŵr Cymru Cyfyngedig (“the operator”),

whose registered office is
Linea
Fortran Road
St Mellons
Cardiff
CF3 0LT

company registration number 02366777

to operate a water discharge activity at
St. Asaph Wastewater Treatment Works
Opposite Holiday Park
St. Asaph
Denbighshire
LL17 0HY

to the extent authorised by and subject to the conditions of this permit.

The permit variation and consolidation shall take effect from 09/10/2025

	Name
	Date

	Joanne Fitton
	09/10/2025


[bookmark: _Toc392252823]Authorised on behalf of Natural Resources Wales.

Conditions
Management
1.1 [bookmark: _Ref373938749]General management
[bookmark: _Ref373938830]The operator shall manage and operate the activity:
in accordance with a written management system that identifies and minimises risks of pollution so far as is reasonably practicable, including those risks arising from operations, maintenance, accidents, incidents, non-conformances and those drawn to the attention of the operator as a result of complaints; and
using sufficient competent persons and resources.
Records demonstrating compliance with condition 1.1.1 shall be maintained. 
Any person having duties that are or may be affected by the matters set out in this permit shall have convenient access to a copy of the permit.
Operations
Permitted activities
The only activity authorised by the permit is the activity specified in schedule 1 table S1.1.
The site 
The discharge activity shall take place at the discharge point marked on the site plan at schedule 7 to this permit, and as listed in table S3.2; and, the operating techniques that are the subject of conditions prefixed by 2.3 shall be applied at the locations shown, or otherwise described, in schedule 7.
Operating techniques
The operator shall comply with the relevant requirements of the Urban Waste Water Treatment (England and Wales) Regulations 1994.
The activity shall, subject to the conditions of this permit, be operated using the techniques and in the manner described in the documentation specified in schedule 1, table S1.2, unless otherwise agreed in writing by Natural Resources Wales.
      
(a) The discharge in schedule 3 table S3.3b shall consist solely of biologically treated sewage effluent which has been disinfected by means of ultra violet (UV) radiation as specified in that table.
(b) The full dose limit in schedule 3 table S3.3b must be exceeded in at least 99% of the specified measurements in the period specified in schedule 3 table S3.3b.
(c) No more than 10% of measurements taken consecutively during any 24 hour period from midnight to midnight should fall below the 50% dose limit specified in schedule 3 table S3.3b.
(d) In the event of a failure of the flow monitor and/or UV used in the control of the UV dosing system:	
(i) the maximum available number of duty banks of UV lamps shall be automatically activated;
(ii) the minimum applied UV dose at maximum effluent flow rates calculated using the 5%ile transmittance shown in schedule 3 table S3.3b, shall not be less than the full dose limit shown in that table.
(e) There shall be no failure to achieve the full dose limit in schedule 3 table S3.3b which is as a result of planned maintenance.
Improvement programme
The flow passed forward monitoring readings required by condition 3.3.1 and tables S3.1 and S3.4 must be taken every two minutes where:
the overflow is directly pumped to a storm tank, unless otherwise agreed in writing by Natural Resources Wales; or
the operator has received the written agreement of Natural Resources Wales to move to monitoring every two minutes from a specified date; or
From 31 March 2026, unless another date is agreed in writing by Natural Resources Wales, the flow passed forward monitoring readings required by condition 3.3.1 and tables S3.1 and S3.4 must be taken every two minutes unless the operator can demonstrate there are sufficient 15-minute readings to assess compliance with the flow passed forward limit in table S3.1.
Emissions and monitoring
Emissions to water
The limits given in schedule 3 table S3.1 shall not be exceeded.
The limits in schedule 3 table S3.1 to which this condition applies may be exceeded where: in any series of samples of the discharge taken at regular but randomised intervals in any period of twelve consecutive months as listed in column 1 of schedule 3A, no more than the relevant number of samples, as listed in column 2 of schedule 3A, exceed the applicable limit for that relevant parameter. For relevant parameters subject to schedule 3C the assessment is based on a fixed calendar year from 1 January to 31 December inclusive.

For the emission limits in schedule 3 table S3.1 to which this condition applies, no sample of the discharge taken at a time when unusual weather conditions are adversely affecting the operation of the waste water treatment works, shall be taken into account in deciding whether or not the emission limit has been complied with.
On any occasion where unusual weather conditions adversely affect the operation of the waste water treatment works, the operator shall use its best endeavours to mitigate that adverse effect.
For any sample of the discharge taken to be considered for the purposes of (a) above, the operator shall notify Natural Resources Wales in writing within 14 days of becoming aware that an emission limit has been exceeded. That notification shall include a full description of the unusual weather conditions and their impact on the operation of the works.

For the emission limits in schedule 3 table S3.1 to which this condition applies, no sample of the discharge taken at a time when abnormal operating conditions are adversely affecting the operation of the waste water treatment works, shall be taken into account in deciding whether or not the emission limit has been complied with.
On any occasion where abnormal operating conditions adversely affect the operation of the waste water treatment works, the operator shall use its best endeavours to mitigate that adverse effect.
For any sample of the discharge taken to be considered for the purposes of (a) above, the operator shall notify Natural Resources Wales in writing within 14 days of becoming aware that an emission limit has been exceeded. That notification shall include a full description of the abnormal operating conditions and their impact on the operation of the works.
The permitted Dry Weather Flow limit in schedule 3 table S3.1 is set at the operator’s planned annual 80% exceeded daily volume discharged. 
For compliance purposes an exceedance shall be recorded for a calendar year only when the limit in effect on 31 December of that calendar year is exceeded by 90% or more of the ‘good’ recorded Total Daily Volumes in that calendar year. 
Until 1 January 2026 
If an exceedance of the Dry Weather Flow limit is recorded in a calendar year then the operator shall, as soon as is practicable, investigate the reasons for the exceedance. 
The operator shall report the reasons for the exceedance to Natural Resources Wales and the steps that it proposes to take to restore compliance. 
An exceedance of the Dry Weather Flow limit shall not be recorded as a failure of the Dry Weather Flow limit in that calendar year if the operator takes appropriate steps to restore compliance. 
From 1 January 2026 
The limit has been complied with in an assessment calendar year unless; 
(i) the limit was exceeded in the compliance assessment calendar year and, 
(ii) two or more exceedances have occurred in the preceding 4 calendar years. 
At least 95% of all flow passed forward readings taken in any calendar year while the overflow to storm tank is operating must be equal to or greater than 92% of the flow passed forward limit specified in schedule 3 table S3.1. 
For the purpose of this condition the following readings shall not be used in the assessment.
data that is not ‘good’ data; or
the first flow reading taken after the start of each overflow event; or
Readings taken when the overflow to the storm tank is operating to facilitate regular planned maintenance, non-routine planned maintenance or non-routine un-planned maintenance, subject to the written agreement of Natural Resources Wales; or
Readings taken when the overflow to the storm tank is operating as a result of a discharge which another person caused or knowingly permitted to be made into the sewer or works, and the operator either was not bound to receive the discharge into the sewer or works or was bound to receive it there subject to conditions which were not observed, and the operator could not reasonably have been expected to prevent the discharge into the sewer or works, subject to the written agreement of Natural Resources Wales.
For any readings to be considered by Natural Resources Wales for the purposes of 3.1.6 (a) (iii) above,
the regular planned maintenance, non-routine planned maintenance or non-routine un-planned maintenance must not have resulted in a discharge from the storm tanks; and
the storm tanks must have been emptied as soon as reasonably practicable and before any further overflow into them occurs; and
the operator must have pre-scheduled the regular planned maintenance and included it in a maintenance programme available for inspection upon request by Natural Resources Wales; and
the operator must have notified Natural Resources Wales in writing at least 5 working days before commencing any non-routine planned maintenance and, within 14 days of completing the non-routine planned maintenance, have submitted a full description of its impact on the operation of the storm tanks to Natural Resources Wales; and
the operator must have notified Natural Resources Wales before commencing any non-routine un-planned maintenance and, within 14 days of completing the non-routine un-planned maintenance, have submitted a full description of the work carried out and its impact on the operation of the storm tanks to Natural Resources Wales; and
the non-routine un-planned maintenance was not required to be carried out due to the act or default of the operator, its agents, representatives, officers, employees or servants
For any readings to be considered for the purposes of 3.1.6 (a) (iv) above, the operator must have notified Natural Resources Wales as soon as reasonably practicable and must have used their best endeavours to minimise any adverse impact on the operation of the storm tanks.
Records demonstrating that the requirements of 3.1.6 (a), (b) and (c) above have been met shall be maintained
Emissions of substances not controlled by emission limits
The operator shall take appropriate measures to minimise so far as reasonably practicable the polluting effects of the emissions of substances in the discharge not controlled by emission limits (excluding odour).
Monitoring 
The operator shall, unless otherwise agreed in writing by Natural Resources Wales, undertake the monitoring specified in the following tables in schedule 3 to this permit:
point source emissions specified in tables S3.1 and S3.4;
inlet quality specified in tables S3.1 and S3.4.
efficacy monitoring specified in tables S3.4 and S3.5.
The operator shall maintain records of all monitoring required by this permit.
Monitoring equipment, techniques, personnel and organisations employed for the emissions monitoring programme and the environmental or other monitoring specified in condition 3.3.1 shall have either MCERTS certification or MCERTS accreditation (as appropriate), where available, unless otherwise agreed in writing by Natural Resources Wales.
Accessible monitoring points shall be provided and maintained to enable the emissions monitoring programme and the environmental or other monitoring to be carried out at the monitoring points specified in table S3.4 of schedule 3 and shown marked on the site plan in schedule 7. 
The monitoring programme for the parameters subject to schedule 3B shall be:
pre-scheduled to cover a calendar year and the programme recorded before the start of a calendar year sample period; and
samples collected at approximately equal intervals during the year, including samples from different days of the week and different times. Approximately 10% of samples should be outside the normal sampling window which is 9am-3pm, Monday to Friday.
After becoming aware, or following a notification that a sample has not been taken on the schedule 3B Monitoring Programme pre-scheduled date, or is lost, or a result for that sample cannot be reported, the operator shall record the details and reschedule the sample.
The monitoring programme for the parameters subject to schedule 3C shall be: 
(a) pre-scheduled before each calendar year; 
(b) Unless otherwise agreed in writing by Natural Resources Wales, the operator shall submit the monitoring programme for the following calendar year to Natural Resources Wales before the 1st of December; and 
(c) samples must be collected at approximately equal intervals during the year from different days of the week and approximately 10% of samples should be taken at weekends. 
Unless otherwise agreed in writing by Natural Resources Wales, after becoming aware, or following notification that a sample has not been taken on the schedule 3C Monitoring Programme pre-scheduled date, or is lost, or a result for that sample cannot be reported, the operator shall notify Natural Resources Wales of the missed event and the reschedule date as soon as reasonably practicable. 
The Operator shall take appropriate measures to ensure that the event recorder remains fully operational at all times within the reference period specified in table S3.1. Any failures shall be remedied as soon as reasonably practicable.

(a) Total Daily Volumes shall be calculated from the average of the available ‘good’ 15-minute flow readings taken from midnight to midnight where; 
Total Daily Volume (m3) = {Sum of ‘good’ readings (l/s) / number of ‘good’ readings} x {86,400 (s) /1000}. 
Where there are 87 or more ‘good’ 15-minute flow readings the Total Daily Volume shall be reported as ‘good’, where there are 1 – 86 ‘good’ readings it shall be reported as ‘suspect’ and where there are no ‘good’ readings as ‘missing’. 
(b) The operator shall record all failures of the flow measurement system and any other breaks in the flow record and the reasons for all issues, failures and breaks that lead to missing or suspect Total Daily Volume records and all steps taken to prevent a re-occurrence. 
(c) There shall be no more than 37 days and/or no more than 14 consecutive days with ‘suspect’ or ‘missing’ Total Daily Volumes in a calendar year, unless otherwise agreed in writing by Natural Resources Wales. 
(d) All 15-minute flow readings shall be flagged as ‘good’, ‘suspect’ or ‘missing’ using an appropriate methodology set out in the operator`s flow monitoring quality management system.
The operator shall, for the flow passed forward and overflow operation monitoring required by condition 3.3.1 and table S3.1 to assess ‘flow passed forward’ limit compliance:
have appropriate systems in place that allow them to detect and record all issues and failures of the monitoring systems, and any other breaks in the data; and
flag all monitoring data as ‘good’, ‘suspect’ or ‘missing’ using an appropriate methodology set out in the operator`s quality management system; and
where ‘good’ flow or overflow operation monitoring data is not recorded for at least 90% of a day the operator shall as far as is reasonably practicable determine and record the reasons why and the steps taken to prevent a re-occurrence; and
The operator shall take all reasonable measures to return the flow and/or overflow operation monitoring equipment to normal operation as soon as reasonably practicable after becoming aware of a failure.
For the flow and overflow operation monitoring required by condition 3.3.1 and table S3.1 to assess ‘flow passed forward’ compliance, and unless otherwise agreed in writing by Natural Resources Wales, there shall be:
no more than 14 consecutive days in any calendar year where ‘good’ flow data are recorded for less than 90% of each day; and
no more than 14 consecutive days in any calendar year where ‘good’ overflow operation data are recorded for less than 90% of each day; and
no more than 37 days in any calendar year that do not have both ‘good’ flow data recorded for at least 90% of each day and ‘good’ overflow operation data recorded for at least 90% of each day.
The flow passed forward monitoring specified in table S3.1:
shall be capable of recording the flow passed forward with a total uncertainty within +/- 8% at the overflow setting specified in table S3.3; and
shall have its total uncertainty assessed as soon as reasonably practicable following MCERTS certification or recertification and in addition whenever a significant change occurs that may impact the total uncertainty; and
all assessment reports confirming the total uncertainty shall be retained for at least six years and provided to Natural Resources Wales within 28 days unless otherwise agreed in writing by Natural Resources Wales.
Continuous recorders, with on-site visual display from which readings may be readily obtained, shall be provided and maintained by the operator and the following shall be measured and recorded at 15 minute intervals:
(f)      the instantaneous flow rate through each UV irradiation channel;
(g) the instantaneous applied UV dose for each UV irradiation channel;
(h) the instantaneous measured UV transmittance at the inlet to the UV irradiation plant;
(i) any other parameters used in calculating the UV dose.
Information
Records
All records required to be made by schedule 3, 4 and 5 to this permit shall:
be legible;
be made as soon as reasonably practicable;
if amended, be amended in such a way that the original and any subsequent amendments remain legible, or are capable of retrieval; and
be retained, unless otherwise agreed in writing by Natural Resources Wales, for at least 10 years from the date when the records were made. 
The operator shall maintain convenient access, in either electronic or hard copy, to the records, plan and management system required to be maintained by this permit. 
Reporting
The operator shall send all reports and notifications required by the permit to Natural Resources Wales using the contact details supplied in writing by Natural Resources Wales.
Within the time period after the end of the reporting period specified in schedule 4 table S4.1 the operator shall, unless otherwise agreed in writing by Natural Resources Wales, submit reports of the monitoring and assessment carried out in accordance with the conditions of this permit, as follows:
in respect of the parameters and monitoring points specified in schedule 4 table S4.1;
for the reporting periods specified in schedule 4 table S4.1 and using the forms specified in schedule 4 table S4.2; and
giving the information from such results and assessments as may be required by the forms specified in those tables.
Notifications
Natural Resources Wales shall be notified as soon as reasonably practicable following detection, within the site of the regulated facility of:
(a) any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution; and
any breach of a limit specified in schedule 3 table S3.1 (including individual exceedances of limits which are covered by condition 3.1.2).
Any other significant adverse environmental effects, which may have been caused by the activity, shall also be notified to Natural Resources Wales as soon as reasonably practicable following detection.
The information provided under condition 4.3.1 shall be supported by sending the information listed in schedule 5 to this permit within the time period specified in that schedule.
Where Natural Resources Wales has requested in writing that it shall be notified when the operator is to undertake monitoring and/or spot sampling specified in schedule 3B & 3C, the operator shall inform Natural Resources Wales when the relevant monitoring and/or spot sampling is to take place. The operator shall provide this information to Natural Resources Wales at least 14 days before the date the monitoring is to be undertaken.
Natural Resources Wales shall be notified within 14 days of the occurrence of the following matters, except where such disclosure is prohibited by Stock Exchange rules:
Where the operator is a registered company:
any change in the operator’s trading name, registered name or registered office address; and
any steps taken with a view to the operator going into administration, entering into a company voluntary arrangement or being wound up.
Where the operator is a corporate body other than a registered company:
any change in the operator’s name or address; and
any steps taken with a view to the dissolution of the operator.
Where the operator proposes to make a change in the nature of the activity by increasing the concentration of, or the addition of, or allowing the introduction of, a substance to the activity to an extent that the operator considers could have a significant adverse environmental effect on the receiving waters, and the change is not permitted by emission limits specified within schedule 3 table S3.1 or the subject of an application for approval under the EP Regulations or under the terms of this permit:
Natural Resources Wales shall be notified in writing at least 14 days before the increase or addition or allowing the introduction; and
the notification shall contain a description of the proposed change.
The operator shall inform Natural Resources Wales in writing of any change, or proposed change, to the population equivalent such as would make a material change to the application of the Regulations and shall, on request, inform Natural Resources Wales in writing of the actual population equivalent. 
Interpretation
In this permit the expressions listed in schedule 6 shall have the meaning given in that schedule.
In this permit references to reports and notifications mean written reports and notifications, except where reference is made to notification being made “as soon as reasonably practicable”, in which case it may be provided by telephone.


Schedule 1 – Operations 
	Table S1.1 Activities

	Description of activity
	Limits of specified activity

	Discharge of secondary treated sewage effluent subject to seasonal disinfection by ultraviolet irradiation via Final Effluent Discharge Point
	Disinfection will take place as described in table S3.3b.
There are no storm discharges to the environment allowed by this permit and the last in line storm discharge is regulated by permit CM0147801.



	Table S1.2 Operating techniques

	Description of documentation
	Parts
	Date Received

	Standstill permit limit monitoring and reporting
	This assessment will take the form of effluent spot sampling together with upstream and downstream river sampling at current OSM frequency
· Parameter Nickel
	19/06/2020




Schedule 2 – Waste types, raw materials and fuels
Schedule 2 not in use.


Schedule 3 – Emissions and monitoring
	Table S3.1 Point Source emissions to water (other than sewer) – emission limits and monitoring requirements

	Effluents and discharge points
	Parameter  
	Limit (including unit)
	Reference Period
	Limit of effective range
	Monitoring frequency
	Compliance Statistic

	Secondary treated sewage effluent subject to seasonal disinfection by ultra violet irradiation via Final Effluent Discharge Point
	Dry weather flow
	1650 m3/day


	Total daily volume
	N/A                                                                
	Continuous
	Conditions 3.1.5 and 3.3.10 apply

	
	15-minute instantaneous or averaged flow
	No limit set. Record as l/s
	15 minutes
	N/A
	Continuous
	N/A

	
	ATU-BOD as O2
	20 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table
(Conditions 3.1.2 and 3.1.3 apply)

	
	ATU-BOD as O2
	56 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Maximum
(Condition 3.1.3 applies)

	
	Suspended solids (measured after drying at 105°C)
	30 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Look up table
(Conditions 3.1.2 and 3.1.3 apply)

	
	Suspended solids (measured after drying at 105°C)
	77 mg/l
	Instantaneous (spot sample)
	N/A
	As specified in schedule 3B
	Maximum
(Condition 3.1.3 applies)

	
	Visible oil or grease
	No significant trace present so far as is reasonably practicable
	Instantaneous (visual examination)
	N/A
	N/A
	No significant trace
(Condition 3.1.3 applies)

	
	ATU-BOD as O2 (UWWTR)
	Minimum of 70 % removal compared to influent
	24-hour composite
	To be compliant a sample has to meet the 70% removal standard or the 25 mg/l limit not both 
	As specified in schedule 3C 
	Look up table
(Conditions 3.1.2 and 3.1.4 apply) 

	
	ATU-BOD as O2 (UWWTR)
	25 mg/l
	
	
	
	

	
	ATU-BOD as O2 (UWWTR)
	50 mg/l
	24-hour composite
	This limit does not apply if a sample has met the 70% removal standard
	As specified in schedule 3C

	Maximum
(Condition 3.1.4 applies)

	
	COD as O2 (UWWTR)
	Minimum of 75 % removal compared to influent
	24-hour composite
	To be compliant a sample has to meet the 75% removal standard or the 125 mg/l limit not both 
	As specified in schedule 3C
	Look up table
(Conditions 3.1.2 and 3.1.4 apply) 

	
	COD as O2 (UWWTR)
	125 mg/l
	
	
	
	

	
	COD as O2 (UWWTR)
	250 mg/l
	24-hour composite
	This limit does not apply if a sample has met the 75% removal standard 
	As specified in schedule 3C

	Maximum
(Condition 3.1.4 applies)

	
	Flow passed forward 
	60 l/s
	15-minute except where 2-minute required by condition 2.4.1
	N/A
	Continuous 15-minute instantaneous or averaged flow except where 2-minute required by 2.4.1
	Minimum
Condition 3.1.6 applies

	
	Overflow operation (into storm storage) monitoring yes/no or start and end times
	N/A
	N/A
	N/A
	2-minute where yes/no or whenever overflow operates where start and end times
	N/A

	
	Overflow operation (into storm storage) monitoring status (operational / not operational)
	N/A
	N/A
	N/A
	2-minute or whenever operational status changes
	N/A



	Table S3.2 Discharge points

	Effluent Name
	Discharge Point
	 Discharge point NGR
	Receiving water/Environment

	Secondary treated sewage effluent subject to seasonal disinfection by ultraviolet irradiation
	Final Effluent Discharge Point
	SJ 03220 75070
	Afon Elwy



	Table S3.3 Storm sewage discharge settings

	Table S3.3 not in use.



	Table S3.3b UV process details and process limits 

	Effluents and discharge points
	UV source
	Dose type
	Full dose mJ/cm2 (see condition 2.3.3(b))
	50% dose mJ/cm2 (see condition 2.3.3(c))
	Effective dates
	5%ile transmittance

	Secondary treated sewage effluent subject to seasonal disinfection by ultraviolet irradiation via Final Effluent Discharge Point
	Broad spectrum medium pressure artificial UV source with at least 85% of available UV radiation emitted in the wavelength range 200 to 300nm 
	Applied
	24
	12
	48 hours prior to local schools Easter fortnight holiday to 21st Oct inclusive 
	45%



	Table S3.4 Monitoring points

	Effluents and discharge points
	Monitoring type
	Monitoring point NGR
	Monitoring point reference

	Secondary treated sewage effluent subject to seasonal disinfection by ultraviolet irradiation via Final Effluent Discharge Point
	UWWTR inlet sampling
	SJ 03308 75126
	UWWTR Inlet Sample Point

	
	Final effluent sampling
	SJ 03246 75102
	Final Effluent Sample Point

	
	Post UV treatment monitoring
	SJ 03246 75102
	UV Monitoring Point (Post-treatment)

	
	UV irradiation channel monitoring as specified by condition 3.3.14
	SJ 03246 75102
	UV Monitoring Point (Post-treatment)

	
	MCERTS continuous flow monitoring
	SJ 03254 75098
	MCERTS Flow Monitoring Point

	
	UWWTR sampling
	SJ 03246 75102
	UWWTR Sample Point

	
	Flow passed forward monitoring
	SJ 03301 75141
	MCERTS FPF Monitoring Point

	
	Overflow operation (into storm storage) monitoring 
	SJ 03264 75079
	EDM to Storm Tank Monitoring Point




	Table S3.5 UV efficacy monitoring point requirements  

	Monitoring type
	Parameters
	Monitoring frequency

	Pre UV treatment monitoring
	No monitoring
	As specified for sanitary parameters in table 3B.
Monitoring for all parameters in table S3.5 to coincide.

	UV Irradiation channel monitoring
	Instantaneous flow rate
Applied dose
	

	Post UV treatment monitoring
	Esherichia Coli (E.coli) 
Intestinal Enterococci 
Suspended solids
	



Schedule 3A - Look up table
	Look up table

	[bookmark: _Hlt511551491]Number of samples taken in any period of 12 months
	Maximum number of samples permitted to exceed limit for given parameter

	4–7  
	 1

	8–16
	 2

	17–28 
	 3

	29–40 
	 4

	41–53  
	 5

	54–67  
	 6

	68–81  
	 7

	82–95 
	 8

	96–110 
	 9

	111–125  
	 10

	126–140  
	 11

	141–155  
	 12

	156–171  
	 13

	172–187 
	 14

	188–203  
	 15

	204–219  
	 16

	220–235  
	 17

	236–251 
	 18

	252–268 
	 19

	269–284  
	 20

	285–300  
	 21

	301–317 
	 22

	318–334  
	 23

	335–350 
	 24

	351–365 
	 25



Schedule 3B - OSM tier 3 sampling frequency
	Parameter
	‘Normal frequency’ of samples per year
	Reduced Sampling frequency after 12 consecutive months of numeric permit compliance, samples per year or pro rata over the remainder of a year
	On numeric limit failure return to normal frequency as soon as reasonably practicable, samples per 12 months1
	Out of hours samples

	Sanitary

	24
	12
	24
	For 24 samples 2 out of hours samples per annum

	Non sanitary

	12
	12
	12
	For 12 samples 1 out of hours sample per annum


1 For UV efficacy monitoring use sanitary frequency and increase following failure of UV requirements only.

Schedule 3C – Urban Waste Water Treatment Regulations sampling frequency
	Population equivalent
	Samples per year
	Reduced sampling frequency after a year without an UWWTR exceedance or failure, samples per year
	Following an UWWTR exceedance or failure return to the higher frequency in the year that follows, samples per year

	2,000 to 9,999

	12
	4
	12

	10,000 to 49,999

	12
	N/A
	N/A

	50,000 or over

	24
	N/A
	N/A



Schedule 4 – Reporting
Parameters, for which reports shall be made, in accordance with conditions of this permit, are listed below.
	Table S4.1 Reporting of monitoring data

	Parameter
	Monitoring point reference
	Reporting period
	Period begins

	Dry Weather Flow (daily flows total)
	MCERTS Flow Monitoring Point
	Annually
Report to be submitted within 2 months of the end of the calendar year
	1st January

	15-minute flow
	MCERTS Flow Monitoring Point
	Reports to be provided to Natural Resources Wales upon request 
Report to be submitted within 28 days unless otherwise specified in writing by Natural Resources Wales
	Upon request by Natural Resources Wales

	UWWTR - ATU-BOD as O2, COD as O2
	UWWTR Inlet Sample Point
and
UWWTR Sample Point
	Monthly
Report to be submitted within 28 days 
	1st of month

	Operator Self-Monitoring - ATU-BOD as O2, suspended solids (measured after drying at 105°C)
	Final Effluent Sample Point
	Quarterly
Report to be submitted within 28 days
	1st of month

	Operator Self-Monitoring summary report
	Final Effluent Sample Point
	Annually
Report to be submitted within 2 months of the end of the calendar year
	1st January

	Disinfection efficacy
Parameters required by conditions 2.3.3, 3.3.1, 3.3.14 and table S3.5
	UV Monitoring Point (Post-treatment)
	Quarterly 
Report to be submitted within 2 months
	1st January, 1st April, 1st July, 1st October

	Flow passed forward monitoring
	MCERTS FPF Monitoring Point
	Reports to be provided to Natural Resources Wales upon request 
Report to be submitted within 28 days unless otherwise specified in writing by Natural Resources Wales 
	Upon request by Natural Resources Wales 


	Overflow operation (into storm storage) yes/no or start and end times
	EDM to Storm Tank Monitoring Point
	Reports to be provided to Natural Resources Wales upon request 
Report to be submitted within 28 days unless otherwise specified in writing by Natural Resources Wales 
	Upon request by Natural Resources Wales 


	Overflow operation (into storm storage) monitoring status (operational / not operational)
	EDM to Storm Tank Monitoring Point
	Reports to be provided to Natural Resources Wales upon request 
Report to be submitted within 28 days unless otherwise specified in writing by Natural Resources Wales 
	Upon request by Natural Resources Wales 


	Flow passed forward and overflow operation monitoring annual report
	MCERTS FPF Monitoring Point 
and
EDM to Storm Tank Monitoring Point
	From 01/01/2026:
Annually
Report to be submitted within 2 months

	1st January 






	Table S4.2 Reporting forms

	Parameter
	Reporting format

	Dry Weather Flow (daily flows total)
	Electronic format specified by Natural Resources Wales

	15-minute flow
	Electronic format specified by Natural Resources Wales

	UWWTR – ATU-BOD as O2, COD as O2
	Electronic format specified by Natural Resources Wales

	OSM - ATU-BOD as O2, suspended solids (measured after drying at 105°C)
	Quarterly - Electronic format specified by Natural Resources Wales 

	Operator Self-Monitoring summary report
	Annually - Summary report of compliance with the monitoring programme specified in Table 3.1 and schedule 3B in a format specified by Natural Resources Wales  

	Disinfection efficacy
	Form as agreed in writing by Natural Resources Wales

	Investigation into the operation of the settled storm overflow
	Electronic format as agreed in writing by Natural Resources Wales. 

	Flow passed forward monitoring
	Electronic format specified by Natural Resources Wales

	Overflow operation (into storm storage) yes/no or start and end times
	Electronic format specified by Natural Resources Wales

	Overflow operation (into storm storage) monitoring status (operational / not operational)
	Electronic format specified by Natural Resources Wales

	Flow passed forward and overflow operation monitoring annual report
	Annual report format as specified by Natural Resources Wales



Schedule 5 – Notification 
These pages outline the information that the operator must provide. 
Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.
If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.
Part A
	Permit Number
	CM0078101

	Name of operator
	Dŵr Cymru Cyfyngedig

	Location of Facility
	St. Asaph Wastewater Treatment Works, Opposite Holiday Park, St. Asaph, Denbighshire, LL17 0HY

	Time and date of the detection 
	



	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution.

	To be notified within 24 hours of detection unless otherwise agreed in writing by Natural Resources Wales.

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released/type or nature of sewage released
	

	Best estimate of the quantity or rate of release of substances and/or duration of discharge
	

	Best estimate of the environmental impact of the discharge
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	





	(b) Notification requirements for the breach of a limit specified in schedule 3 table S3.1 (including individual exceedances of limits which are covered by condition 3.1.2).

	The information specified below is to be notified to Natural Resources Wales as soon as reasonably practicable following detection.

	Monitoring point reference/ source
	

	Self-monitoring regime (where relevant)
	e.g. OSM/UWWTR/EDM

	Type of failure 
	e.g. LUT failure/LUT exceedance/upper tier/other

	Date of sample/event
	

	Parameter
	

	Result and units
	

	Limit and units
	



	(c) Notification requirements for the detection of any significant adverse environmental effect.

	To be notified within 24 hours of detection.

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B – to be submitted as soon as reasonably practicable unless otherwise agreed in writing by Natural Resources Wales
	Any more accurate information on the matters for notification under Part A.
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident/breach/exceedance
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	



	Name*
	

	Post
	

	Signature
	

	Date
	


* authorised to sign on behalf of the operator
Schedule 6 – Interpretation 
“abnormal operating conditions” include but are not limited to, the circumstances described in Regulation 40(1) of, or paragraph 6(5) of Schedule 21 to, the Environmental Permitting Regulations 2016 (illegal discharge to sewer), unusual weather, or during a defined period where the permit authorising the permitted activity has been varied for reasons such as capital works construction.
“accident” means an accident that may result in pollution.
“annually” means once every year.
“application” means the application for this permit, together with any additional information supplied by the operator as part of the application and any response to a notice served under Schedule 5 to the EP Regulations.
“appropriate measures” for the purposes of the emission of substances not controlled by emission limits condition (condition 3.2.1) do not require the operator to undertake treatment to a level beyond that specified in schedule 1 table S1.1, or to carry out routine monitoring for substances not controlled by emission limits.
“ATU-BOD as O2” means the biochemical oxygen demand (measured after 5 days at 20°C with nitrification suppressed by the addition of allylthiourea).
“block-counted spill” one or more overflow events within a period of 12 hours or less will be considered to be one spill, one or more overflow events extending over a period of greater than 12 hours up to 36 hours will be considered to be 2 spills. Each subsequent 24-hour duration counts as 1 additional spill and the whole of the 24-hour block is included. 
“COD as O2” means the chemical oxygen demand (measured using the standard dichromate procedure).
“disinfection” means the use of a process designed specifically to reduce the number of viable, potentially infectious micro-organisms in the effluent.
“emissions of substances not controlled by emission limits” means emissions of substances to air, water or land from the permitted activities, which are not controlled by an emission limit.
“EP Regulations” means The Environmental Permitting (England and Wales) Regulations SI 2016 No.1154 and words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.
“event recorder” a recorder which records the start time and end time of individual overflow events.
“flow passed forward” for the purposes of condition 3.1.6 means, the rate of flow (litres per second) of the waste water arriving at the overflow from its upstream collection system and passed forward to the continuation flow. It does not include any flows that have already been passed forward by the overflow and are reintroduced to the incoming flow upstream of the overflow from any point downstream of it.
“Formula A” is defined as (PG+I+E) + 1360P + 2E litres/day.  Where P = population served, G = water consumption per head per day (litres/head/day) I = infiltration (litres/day) E = trade effluent flow to sewer (litres/day)
“good flow data for at least 90% of each day” means at least 87 fifteen minute or 648 two-minute flow readings are flagged as good in a day.
“good overflow operation data for at least 90% of each day” means at least 648 two-minute overflow operation readings are flagged as good or the overflow operation duration monitor is operational for at least 1,296 minutes in a day.
“MCERTS” means the Environment Agency’s Monitoring Certification Scheme.
“minimum screen capacity flow” means the minimum flow passed through the screens to the outfall when the screen bypass operates. 
“monitoring frequency” as used in Table S3.1 in the context of event duration monitoring is the temporal interval at which a change in state between no discharge and discharge is to be detected.
“Natural Resources Wales” means the Natural Resources Body for Wales established by article 3 of the Natural Resources Body for Wales (Establishment) Order 2012. The Natural Resources Body for Wales (Functions) Order 2013 transferred the relevant functions of the Countryside Council for Wales, and functions of the Environment Agency and the Forestry Commission in Wales to the Natural Resources Body for Wales.
“Non-routine planned maintenance” means maintenance, inspection, refurbishment, or replacement of plant and equipment carried out in accordance with a documented maintenance plan, which is foreseeable and can be planned at least 5 working days in advance.
“Non-routine un-planned maintenance” means extra-ordinary maintenance to carry out inspection, refurbishment, or replacement of plant and equipment that is unforeseeable and cannot be planned at least 5 working days in advance.
“overflow” for the purposes of schedule 7, overflow means the weir or orifice or other control which directs excess flow away from the continuation sewer when the flow exceeds the overflow setting due to rainfall and/or snowmelt.
“overflow event” any individual operation, of any duration, of the event recorder or any recorded discharge of sewage from the outfall.
“overflow setting” means the minimum flow passed forward to the continuation sewer when the overflow operates.
“quarter” means a calendar year quarter commencing on 1st January, 1st April, 1st July or 1st October.
“Regular planned maintenance” means scheduled maintenance, inspection, refurbishment, or replacement of plant and equipment carried out periodically and in accordance with a documented maintenance plan, it does not have to take place on specified dates.
“significant pollution” means a high level impact incident as indicated by NRW incident classification system.
[bookmark: OLE_LINK1][bookmark: OLE_LINK2]“significant spill” any spill that has not been demonstrated to have been, or measured as being, less than 50 m3 in volume.
“Total uncertainty” means the combined (total) uncertainty of the flow rate measurement due to the flow monitoring installation, as determined by an MCERTS inspector, and uncertainties induced between the overflow and the flow monitor as determined by the operator. Allowances for time delays in flow response through the WwTW are taken into account by condition 3.1.6.
“unusual weather conditions” includes, but is not limited to:
· low ambient temperatures, or the freezing of mechanical equipment in the works;
· significant snow deposits;
· tidal or fluvial flooding;
· weather conditions causing unforeseen loss of power supply to the sewage treatment that could not be ameliorated by the reasonable provision and operation of standby generation facilities.
“Urban Waste Water Treatment (England and Wales) Regulations 1994 (UWWTR)” means Urban Waste Water Treatment (England and Wales) Regulations 1994 SI 2841and the words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.
“year” means calendar year ending 31st December.
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