| DOCUMENT CONTROL |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DOCUMENT PROPERTIES |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Site |  |  |  | Barry West SPS |  |  |  |  |  |  |  |  |  |
| Scheme |  |  |  | Internal OTO – PLC Resilience Upgrade |  |  |  |  |  |  |  |  |  |
| Scheme Code |  |  |  | N/A |  |  |  |  |  |  |  |  |  |
| Document No. |  |  |  | CAF424 – Barry West SPS – PLC Upgrade 2024 V2.1 |  |  |  |  |  |  |  |  |  |
| Design Team |  |  |  | OTO SE |  |  |  |  |  |  |  |  |  |
| DOCUMENT STATUS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Info |  | Review |  |  | Approval |  |  | Enquiry |  | Tender |  | Construction |  |
| Revision History |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rev. | Date |  | Description of Rev. |  |  | Author(s) (Discipline) |  |  | Checkers(s) (Discipline) |  | Approver(s) (Discipline) |  |  |
|  |  |  |  |  |  | Signature |  |  | Signature |  | Signature |  |  |
| V0.00 | 11/11/2021 |  | Initial Draft |  |  | A | G. Price |  |  |  |  |  |  |
| V1.00 | 12/01/2024 |  | Kick-off Review |  |  | A | S. Silva |  | SA | R. Letheby | SA |  | R. Letheby |
| V2.00 | 16/07/2025 |  | Final |  |  | A | S. Silva |  | SA | R. Letheby | SA |  | R. Letheby |
| V2.10 | 18/07/2025 |  | Amendments following PF comments |  |  | A | S. Silva |  | SA | R. Letheby | SA |  | R. Letheby |

| Revision History Discipline / Position Key |  |  |
| --- | --- | --- |
| P – Process Engineer | SP – Senior Process Engineer | LDE – Lead Design Engineer |
| M – Mechanical Engineer | SME – Senior Mechanical & Engineer | PM – Project Manager |
| E – Electrical Engineer | SC – Senior Civil Engineer | PC – Project Co-ordinator |
| C – Civil Engineer | SA – Senior Automation Engineer | DelM – Delivery Manager |
| A – Automation Engineer |  | DM – Design Manager |

Contents

Executive Summary	4

1.	References	5

1.1.	Standard Specifications	5

1.2.	Glossary of Terms	5

2.	Additional Information	6

3.	Control System Overview	7

3.1.	Operation	7

3.2.	Data Network	7

3.3.	Hardware	7

3.4.	SCADA Configuration	8

4.	PLC	9

5.	Barry West SPS MCC	11

5.1.	Docks SPS – Foul Pumps	11

5.2.	Knap SPS – Foul Pumps	13

5.3.	Island PS	15

5.4.	Inlet	19

5.5.	Transfer PS	22

5.6.	Long Sea Outfall PS	26

5.7.	Short Sea Outfall PS	30

5.8.	Storm Tank	34

5.9.	Odour Control	38

5.10.	Site Power Control	40

#### Executive Summary

The Functional Design Specification is a key site document and provides a comprehensive description of the site control system. This is a controlled document - owned by operations. This document is to be updated on an ongoing basis, as required, to provide an accurate and up to date record of the control system. All modifications, regardless of delivery approach, shall be captured within this document. Document status and revision history is recorded within the top of this document. The format outlined within this document shall be adhered to – generic information is in italic font, whilst specific information is normal font. An overview of the control system and operation strategy for the site is provided within section 4. A detailed description of each element of the control system is provided within section 5. Section 6 provides details of the outstation configuration. Supporting information (e.g. Schedules, drawings etc) is appended to this document. As a minimum, a reference is provided but where file size permits, supporting documentation is embedded.

| #### References |  |
| --- | --- |
| ##### Standard Specifications | Control system design is in accordance with the latest version of the following standard specifications. Where conflict exists, priority corporate standards supersede national standards. |
| CORPORATE STANDARDS | - AS427 Industrial Communication Networks Ver. 5.01 - AS430 Standard Function Block Library (Mitsubishi) Ver. 3.17 - AS431 Operator Interface Standard Graphics Part C (Mitsubishi) Ver. 1.03 - AS432 Standard Software Guide Ver. 1.01 - CAF424 FDS Template Ver. 2.01 - ES403 Standard PLC IO Schedule Ver 1.03 - ES403 Programmable Logic Controller Ver. 9.11 - ES404 RTU Installations Ver 7.10 - ES424 Control System Visualisation (SCADA&HMI) Ver. 5.04 |
| NATIONAL STANDARDS | - BS 7671:2008+ A3:2015 Requirements for electrical installations. IEE Wiring Regulations. Seventeenth edition - WEEE Directive |

| ##### Glossary of Terms |  |  |  |
| --- | --- | --- | --- |
| TERM | DESCRIPTION | TERM | DESCRIPTION |
| FAT | Factory Acceptance Test | P&ID | Piping & Instrumentation Diagram |
| FDS | Function Design Specification | PC | Personal Computer |
| FTC | Failed To Close | PID | Proportional, Integral & Derivative |
| FTO | Failed To Open | PLC | Programmable Logic Controller |
| FTR | Failed To Run | PV | Process Variable |
| FTRL | Failed To Reach Limits | RTL | Run Time Logic |
| FTS | Failed To Stop | SAT | Site Acceptance Test. |
| HH | High High Threshold | SCADA | Supervisory Control And Data Acquisition. |
| HI | High Threshold | SDS | System Design Specification |
| HMI | Human Machine Interface | Secs | Seconds |
| ICA | Instrument Control & Automation. | SSS | Software System Specification |
| LL | Low Low Threshold | TBA | To Be Advised By Primary Contractor |
| LO | Low Threshold | TBC | To Be Confirmed By The Client. |
| LOE | Loss Of Echo | UOS | Unless Otherwise Stated. |
| MCC | Motor Control Centre. | UPS | Uninterruptible Power Supply |
| OOR | Out of range | URS | User Requirement Specification |
| OOS | Out Of Service | VSD | Variable Speed Drive. |
| ACB | Air Circuit Breaker | DOL | Direct Online (Motor) |

#### Additional Information

This FDS has been completed based on the existing PLC code that is in operation on site, due to the lack of any existing FDS. No amendments have been made to the control of the asset. Any irregularities that arise in this document in comparison to the specifications at the time of the upgrade are due to the historic control.

| #### Control System Overview |  |
| --- | --- |
| ##### Operation | Normally, the process operates automatically under supervisory control. However, it is possible to manually intervene, overriding automatic control for maintenance purposes or due to extraordinary operating conditions |
| AUTOMATIC CONTROL | Automatic control is primarily achieved by a number of PLCs – typically one dedicated per process area. Each PLC and its full functionality is described within Section 5. Where necessary, PLC control deemed is supplemented with back-up control. Back-up control is achieved via simple electrical connections and overrides PLC automatic control in event of it becoming ineffective. A full description of all backup control is provided within Section 5 |
| MANUAL CONTROL | It is possible to operate an item of plant directly via proprietary local controls provided at the drive, associated control panel or local push button station. Local manual control overrides other control modes – with the exception of safety-related back up control. A full description of all manual control is provided within Section 5. |
| SUPERVISORY CONTROL | Supervisory control is achieved remotely, via a HMI Terminal installed on the Site. Supervisory control allows the operator to interrupt or influence automatic control –however, back-up control will still prevail. A full description of supervisory control is described within Section 5. |

| ##### Data Network |  |
| --- | --- |
| TOPOGRAPHY | N/A |
| TOPOLOGY | N/A |

| ##### Hardware |  |
| --- | --- |
| NETWORK | Westermo L206-F2G – 10 Port Switch – 8 x RJ45, 10/100 BaseTX, 2 x 100/1000 BaseTX SFP Transceivers |
| SCADA | N/A |
| HMI | Mitsubishi GT2715-XTBD – 15" TFT, 65K colour, 1024x768 pixel touch screen |
| PLC | Mitsubishi R08ENCPU – 80K Step Memory IQR CPU |
| RTU | Ovarro S2000 Full with Extended Memory, Main Powered, M2M Comms (TBC) |

| ##### SCADA Configuration |  |
| --- | --- |
| RUN TIME LOGIC (RTL) |  |
| MONNET | N/A |
| UPS SHUTDOWN | N/A |
| UPS BATTERY | N/A |
| PLC WATCHDOG MONITOR | N/A |
| PLC TIMESYNC | N/A |
| NIC MONITOR | N/A |
| COMMUNICATIONS CONFIGURATION | N/A |
| SYSTEM WORKSTATION CONFIGURATION | N/A |
| WORKSTATION SERVER CONFIGURATION | N/A |
| REMOTE ARCHIVER CONFIGURATION | N/A |

| #### PLC |  |
| --- | --- |
| This section provides a comprehensive description of the control philosophies, broken down on a ‘per control group’ basis. It is intended that each section can be read in isolation to aid future reference. In an effort to reduce overall document size, the terms of reference are detailed below only, as opposed to repeating within each section. As the format of each section is identical, the following apply to all sections. |  |
| PROCESS OVERVIEW | Section X.x.1, provides an outline description of the Treatment Process for the Control group being described. The description should, as a minimum, include quantity, type and purpose of all process units and an outline of the general arrangement. Any related process performance parameters critical to design should also be stipulated within this section (eg max FTT, Ammonia consent etc). |
| PLANT OVERVIEW | The table within this section schedules all devices associated with the Control group being described. Specific references are omitted from this table - as they are fully specified within the Tag Database, appended to this document. Note that devices may be repeated within multiple sections if associated with more than one control group. - It is intended that Device Type be limited to a generic description only. Make/Model/Manufacturer etc should be fully specified elsewhere and appended to this document. - Where Valves are being described, generic type description should clarify if modulating/non-modulating and how actuated (eg Electrically Actuated, Solenoid, Pneumatic etc). - Where Motors/Pumps are being described, generic type description should include drive type (eg. Fixed speed, variable speed etc) - It is intended that Device Location describe the relative position within the process (eg Downstream of Inlet Chamber) and, as necessary, the geographical position. - It is intended that Device Purpose describes the specific application of the device. - The Control System Interface should clarify which PLC the device directly communicates with and connection type (eg discrete, Profibus DP etc). Slip ring type connections, across site telemetry links etc should also be highlighted. |
| AUTOMATIC CONTROL | Section 5.x.x.3 contains a high level description of the Automatic Control for the control group being described and forms the basis of functional design. |
| NORMAL AUTOMATIC OPERATION | Normal automatic operation is the intended operation achieved by the PLC when no abnormal conditions are present. As such, the associated plant operates with no operator intervention and would not generate any alarms. The table within section 5.x.x.4 provides a functional description to meet the requirements of automatic control and forms the basis of software design. |
| ABNORMAL AUTOMATIC OPERATION | In event of failure conditions or manual intervention, the PLC will react accordingly in an effort to maintain effective automatic control or halt process in a safe manner. The table in section 5.x.x.5 schedules all abnormal conditions, associated effect to the automatic control system and reset method. |
| BACK-UP CONTROL | Back-up control is instigated when the process operates outside the normal parameters of the automatic control system. The table within section 5.x.x.6 schedules all Process related back-up control for the control group being described. Usually termed ‘hardwired inhibits’ or ‘hard-wired control’, these always interrupt PLC control (automatic and supervisory remote manual control modes) - but not local manual control. The table within section 5.x.x.7 schedules all Safety related back-up control for the control group being described. Usually termed ‘hardwired interlocks’, these always interrupt all other control modes – including local manual control. |
| MANUAL CONTROL | Local manual control interrupts automatic control. However, status is repeated to the PLC so that the automatic control can react, as necessary to avoid spurious alarms or ineffective overall control. Supervisory control is always prevented when in local manual control. The table within section 5.x.x.8 schedules all local manual control for the control group being described. |
| SCADA | The full SCADA configuration is in accordance DCWW standard specification for Operator Interface Standard Graphics. A graphical representation (mimic) of the process is provided and is accessible via all SCADA Clients/Panel PCs. The general arrangement of the mimic will be in a schematic format and be based upon the plant overview for the control group being described. Plant status is displayed on associated faceplate. Selected Plant status will be repeated within the body of the mimic. Alarms are generated for all abnormal conditions associated with the control group being described. Alarms are always displayed in a tabular format in the Alarm Banner, with selected Alarms repeated within the body of the mimic and on associated faceplates. Any trending of data is configured by the user. In addition to remote manual operation/configuration of individual plant (via faceplates), supervisory control facilitates control system adjustments. The table in section 5.x.x.9 schedules all Control system adjustments, selected status and alarms to be repeated on the mimic for the control group being described. Note that the full list of engineering setpoints are excluded from this table. Full details of the SCADA/PLC interface are scheduled within the Tag Database (appended to this document). |

#### Barry West SPS MCC

| ###### Docks SPS – Foul Pumps |  |
| --- | --- |
| Status | FDS |

- PROCESS OVERVIEW

Docks Sewage Pumping Station collects sewage from the surrounding area into a manhole and through a normally open valve into the Foul Sump. Two Duty/Standby pumps then pump the sewage to Barry West SPS – Island PS.

- PLANT OVERVIEW

| Signature | Description | Type | Location | Purpose | Qty | Control System Interface |
| --- | --- | --- | --- | --- | --- | --- |
|  | P1001 – Foul Pump 1 | DOL | Foul Sump | Pump Sewage to Barry West SPS | 1 | Telemetry Control |
|  | P1002 – Foul Pump 2 | DOL | Foul Sump | Pump Sewage to Barry West SPS | 1 | Telemetry Control |

- CONTROL PHILOSOPHY

Foul Pumps P1001 & P1002 Fixed speed Pumps P1001 and P1002 are arranged as a Duty/Standby pair and are controlled locally at the station. They are enabled from Barry West SPS when the Mains Supply at Barry West SPS is healthy. If the Mains has failed then there must be sufficient supply available from the Generators. If any generator has failed then the Foul Pumps at Docks SPS will be inhibited.

- NORMAL AUTOMATIC OPERATION

| Signature | Drive | Enabler(s) | Disabler(s) | Modifier(s) |
| --- | --- | --- | --- | --- |
| S.Silva | Foul Pumps | (Mains Healthy at Barry West SPS OR [Mains Failed & Generator Power Available & NOT No Power For Fouls & Assist Transfer]) & Staggered Start 15 Healthy | Mains Failed at Barry West SPS OR Staggered Start 15 Failed | N/A |

- ABNORMAL AUTOMATIC OPERATION

| Signature | Failure/Abnormal Condition | Resultant Control Action | Reset Method |
| --- | --- | --- | --- |

- BACK UP CONTROL – PROCESS

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- BACK UP CONTROL – SAFETY

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- MANUAL CONTROL

| Signature | Plant | Selection | Actions |
| --- | --- | --- | --- |

- SUPERVISORY CONTROL

| Signature | Setpoint Group | Setpoint | Comment |
| --- | --- | --- | --- |

- TELEMETRY DATA

Nomenclature to be finalised within TagDB. Full configuration to be recorded in accordance with DCWW Document ES404.

| Signature | Name | Type | Priority | Comment |
| --- | --- | --- | --- | --- |
|  | TBC with Storm Tank Upgrade |  |  |  |

- MISCALLANEOUS

N/A

- COMMENTS

| Name | Company | Role | Date | Signature |
| --- | --- | --- | --- | --- |

| ###### Knap SPS – Foul Pumps |  |
| --- | --- |
| Status | FDS |

- PROCESS OVERVIEW

Foul Pumps at the Knap SPS are controlled from Barry West SPS to ensure it won’t pump against a closed valve at Barry West.

- PLANT OVERVIEW

| Signature | Description | Type | Location | Purpose | Qty | Control System Interface |
| --- | --- | --- | --- | --- | --- | --- |
|  | Foul Pump 1 | DOL | Foul Sump | Pump Sewage to Barry West SPS | 1 | Telemetry Control |
|  | Foul Pump 2 | DOL | Foul Sump | Pump Sewage to Barry West SPS | 1 | Telemetry Control |

- CONTROL PHILOSOPHY

Foul Pumps Both Foul Pumps will be inhibited from running when the Emergency Penstock EP2 is closed. As long as the power on site is healthy and the penstock isn’t closed, the foul pumps at Barry Knap will be enabled again.

- NORMAL AUTOMATIC OPERATION

| Signature | Drive | Enabler(s) | Disabler(s) | Modifier(s) |
| --- | --- | --- | --- | --- |
| S.Silva | Knap SPS Foul Pumps | EP2 Open & Staggered Start Complete | EP2 Closed |  |

- ABNORMAL AUTOMATIC OPERATION

| Signature | Failure/Abnormal Condition | Resultant Control Action | Reset Method |
| --- | --- | --- | --- |

- BACK UP CONTROL – PROCESS

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- BACK UP CONTROL – SAFETY

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- MANUAL CONTROL

| Signature | Plant | Selection | Actions |
| --- | --- | --- | --- |

- SUPERVISORY CONTROL

| Signature | Setpoint Group | Setpoint | Comment |
| --- | --- | --- | --- |

- TELEMETRY DATA

Nomenclature to be finalised within TagDB. Full configuration to be recorded in accordance with DCWW Document ES404.

| Signature | Name | Type | Priority | Comment |
| --- | --- | --- | --- | --- |
|  | TBC with Storm Tank Upgrade |  |  |  |

- MISCALLANEOUS

N/A

- COMMENTS

| Name | Company | Role | Date | Signature |
| --- | --- | --- | --- | --- |

| ###### Island PS |  |
| --- | --- |
| Status | FDS |

- PROCESS OVERVIEW

Island Pumping Station collects sewage from the surrounding area into the Foul Sump. Duty/Assist Pump configuration pumps sewage to Barry West SPS inlet. Pumps controlled via ultrasonic level controller. Flow weirs over into Storm Sump when Foul sump is overwhelmed. Storm Sump has 3 Pumps in Duty/Assist/Assist configuration and pumps sewage to Barry West SPS Inlet. Pumps controlled via ultrasonic level controller. All Values, Alarms & Status are displayed and logged on the local HMI. Selected Values, Alarms & Status are also displayed on regional telemetry.

- PLANT OVERVIEW

| Signature | Description | Type | Location | Purpose | Qty | Control System Interface |
| --- | --- | --- | --- | --- | --- | --- |
|  | Foul Pumps P701/2 | DOL (Fixed Speed) | Island Foul Sump | Lifts flow from Foul Sump to Barry West SPS Inlet | 2 | Discrete I/O to PLC |
|  | Foul Sump Level Controller LIT702 | Ultrasonic | Above Island Foul Sump | Measure Foul Sump Level | 1 | Discrete I/O to PLC |
|  | Storm Pumps P801/2/3 | DOL (Fixed Speed) | Island Storm Sump | Storm Conditions | 3 | Discrete I/O to PLC |
|  | Storm Sump Level Controller LIT802 | Ultrasonic | Above Island Storm Sump | Measure Storm Sump Level | 1 | Discrete I/O to PLC |

- CONTROL PHILOSOPHY

Foul Pumps The Foul Pumps are operated in a Duty/Assist configuration, controlled by preset ‘Start’ & ‘Stop’ Levels. Start/Stop Conditions The Duty pump is called to run when the foul sump level (LIT702) is above the duty pump start level set point (Adjustable) for a preset enable time (Adjustable). If the foul sump level (LIT702) falls below the duty pump stop level (Adjustable) for a preset run-on time (Adjustable), then the duty pump will stop. The Assist pump is called to run when the foul sump level (LIT702) is above the assist pump start level set point (Adjustable) for a preset enable time (Adjustable). If the foul sump level (LIT702) falls below the assist pump stop level (Adjustable) for a preset run on time (Adjustable), then the assist pump will stop. If the foul sump level (LIT702) LOE alarm or out of range alarm becomes active then the pumps will stop. A single pump is inhibited upon any of the following: - Pump not healthy - Pump unavailable (selected to ‘Hand’ at panel or ‘Manual’ via HMI) - Pump failed to start - Pump E-Stop operated All Pumps are inhibited upon any of the following: - Mains fail & Generators not available - Foul sump level (LIT702) LOE/OOR Storm Pumps The Storm Pumps are operated in a Duty/Assist/Assist configuration, controlled by preset ‘Start’ & ‘Stop’ Levels. Storm pumps do not run on mains power. Power requirements - Duty Storm pump requires 1 generator to run. - Assist Storm pump requires 2 generators to run - 2nd Assist Storm pump requires 3 generators to run Start/Stop Conditions The Duty pump is called to run when the Storm sump level (LIT802) is above the duty pump start level set point (Adjustable) for a preset enable time (Adjustable). If the Storm sump level (LIT802) falls below the duty pump stop level (Adjustable) for a preset run on time (Adjustable), then the duty pump will stop. The Assist pump is called to run when the Storm sump level (LIT802) is above the assist pump start level set point (Adjustable) for a preset enable time (Adjustable). If the Storm sump level (LIT802) falls below the assist pump stop level (Adjustable) for a preset run on time (Adjustable), then the assist pump will stop. The 2nd Assist pump is called to run when the Storm sump level (LIT802) is above the 2nd assist pump start level set point (Adjustable) for a preset enable time (Adjustable). If the Storm sump level (LIT802) falls below the 2nd assist pump stop level (Adjustable) for a preset run on time (Adjustable), then the 2nd assist pump will stop. If the Storm sump level (LIT802) LOE alarm or out of range alarm becomes active then the pumps will stop. A single pump is inhibited upon any of the following: - Pump not healthy - Pump unavailable (selected to ‘Hand’ at panel or ‘Manual’ via HMI) - Pump failed to start - Pump E-Stop operated - Generator not available All Pumps are inhibited upon any of the following: - Generators not available - Storm sump level (LIT802) LOE/OOR

- NORMAL AUTOMATIC OPERATION

| Signature | Drive | Enabler(s) | Disabler(s) | Modifier(s) |
| --- | --- | --- | --- | --- |
| S.Silva | Duty Foul Pump P701/2 | (Mains supply healthy OR Generator available) & LIT702 Healthy & LIT702 Duty Start level reached & Staggered Start 14 Healthy | (Mains supply failed AND Generator Unavailable) OR LIT702 Failed OR LIT702 Duty Stop level reached OR Staggered Start 14 Failed |  |
| S.Silva | Assist Foul Pump P701/2 | (Mains supply healthy OR Generator available) & LIT702 Healthy & LIT702 Assist Start level reached & Staggered Start 14 Healthy & Duty Pump is Running | (Mains supply failed AND Generator Unavailable) OR LIT702 Failed OR LIT702 Duty Stop level reached OR Staggered Start 14 Failed OR Duty Pump Stopped |  |
|  | Duty Storm Pump P801/2/3 | 1 Generator Available for Duty & LIT802 Duty start level reached | 1 Generator NOT Available for Duty OR LIT802 Duty stop level reached |  |
|  | Assist Storm Pump P801/2/3 | 2 Generators Available for Duty & LIT802 1st Assist start level reached & Duty Pump Running | 2 Generators NOT Available for Duty OR LIT802 1st Assist stop level reached OR Duty Pump Stopped |  |
|  | 2nd Assist Storm Pump P801/2/3 | 3 Generators Available for Duty & LIT802 2nd Assist start level reached & Assist Pump Running | 3 Generators NOT Available for Duty OR LIT802 2nd Assist start level reached OR Assist Pump Stopped |  |

- ABNORMAL AUTOMATIC OPERATION

| Signature | Failure/Abnormal Condition | Resultant Control Action | Reset Method |
| --- | --- | --- | --- |
|  | Power Failure | ALL Foul Pumps Stop | Restoration of mains supply and staggered start sequence |
|  | PLC Watchdog Failed | ALL Foul & Storm Pumps Stop | PLC Watchdog Reset |
|  | Foul Pump Failed | Pump Stop & Standby Pump Start | Auto Reset once cleared at starter via local reset & HMI Reset |
|  | Storm Pump Failed | Pump Stop & Standby Pump Start | Auto Reset once cleared at starter via local reset & HMI Reset |
|  | LIT702 Foul Sump Level Failed | Stop Foul Pumps | Auto Reset when cleared |
|  | LIT802 Storm Sump Level Failed | Stop Storm Pumps | Auto Reset when cleared |

- BACK UP CONTROL – PROCESS

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- BACK UP CONTROL – SAFETY

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- MANUAL CONTROL

| Signature | Plant | Selection | Actions |
| --- | --- | --- | --- |
|  | Foul Pumps (P701/2) | LCP Control Mode switch selected to ‘Hand’ | Start/Stop via Push Buttons |
|  | Storm Pumps (P801/2/3) | LCP Control Mode switch selected to ‘Hand’ | Start/Stop via Push Buttons |

- SUPERVISORY CONTROL

| Signature | Setpoint Group | Setpoint | Comment |
| --- | --- | --- | --- |
|  | Foul Pump Duty Selection | HMI |  |
|  | Foul Pump Duty Start/Stop Level | HMI |  |
|  | Foul Pump Assist Start/Stop Level | HMI |  |
|  | Storm Pump Duty Selection | HMI |  |
|  | Storm Pump Duty Start/Stop Level | HMI |  |
|  | Storm Pump 1st Assist Start/Stop Level | HMI |  |
|  | Storm Pump 2nd Assist Start/Stop Level | HMI |  |

- TELEMETRY DATA

Nomenclature to be finalised within TagDB. Full configuration to be recorded in accordance with DCWW Document ES404.

| Signature | Name | Type | Priority | Comment |
| --- | --- | --- | --- | --- |
|  | TBC with Storm Tank Upgrade |  |  |  |

- MISCALLANEOUS

<insert anything here deemed useful but not applicable to sections above>

- COMMENTS

| Name | Company | Role | Date | Signature |
| --- | --- | --- | --- | --- |

| ###### Inlet |  |
| --- | --- |
| Status | FDS |

- PROCESS OVERVIEW

Foul flow from Island PS passes to the Inlet via the Inlet works Flow meter (FIT1202), this is an open channel meter and the flow is regulated by a downstream penstock (RP0001). Inlet emergency penstock EP2 isolates the works in certain storm conditions.

- PLANT OVERVIEW

| Signature | Description | Type | Location | Purpose | Qty | Control System Interface |
| --- | --- | --- | --- | --- | --- | --- |
|  | Inlet Works Flow FIT1202 | Open Channel (Flume) | Downstream of Island PS | Measure Flow into Transfer PS | 1 | Discrete I/O to PLC |
|  | Inlet Works Regulating Penstock RP0001 | Electrical actuated penstock | Downstream of Inlet Works Flow (FIT1202) | Regulate flow to Transfer PS | 1 | Discrete I/O to PLC |
|  | Emergency penstock – EP2 | Electrical actuated penstock | Inlet | Isolate flow to SPS | 1 | Discrete I/O to PLC |
|  | Inlet Level – LIT902 | Ultrasonic | Inlet | Monitor inlet level | 1 | Discrete I/O to PLC |
|  | Storm Overflow Screens M901-M902 | DOL (Fixed Speed) | Upstream of Fine Screens at Inlet |  | 2 | Discrete I/O to PLC |

- CONTROL PHILOSOPHY

Inlet Flow Flow to the inlet works goes through the open channel Inlet Flume (FIT1202) and is regulated with Regulating Penstock (RP0001) to achieve a flow setpoint made via the HMI. The Regulating Penstock will be controlled using Nudge and Wait. Regulating Penstock The regulating penstock (RP0001) is controlled using Nudge and Wait with setpoints configurable via the HMI. The regulating penstock will close upon the inlet flume flow meter FIT1202 failing or going out of range. And, if the Transfer sump goes High level or out of range. The regulating penstock will reopen on the above conditions being healthy. Emergency Penstock – EP2 This is used to isolate the inlet when either the inlet level (LIT902) or the SSO Sump level (LIT1802) goes to High High level for a preset time. The penstock will be open when Inlet level and SSO Sump level are NOT High High level. If there is a mains failure then EP2 shall close via UPS power depending on SSO Sump level or Inlet Level Overflow Screens When the Town Inlet Level (LIT902) is above the start setpoint for a pre-set time then the Screens with run continuously until the Town Inlet level (LIT902) falls below the stop setpoint for a pre-set time.

- NORMAL AUTOMATIC OPERATION

| Signature | Drive | Enabler(s) | Disabler(s) | Modifier(s) |
| --- | --- | --- | --- | --- |
| S.Silva | Regulating Penstock RP0001 | FIT1202 Healthy & RP0001 Healthy | Close when FIT1202 Failed OR Transfer station high high level for pre-set time | Flow Nudge Wait Control |
| S.Silva | Emergency Penstock – EP2 | Penstock Healthy AND Penstock Auto AND (NOT LSO Level LIT1802 High Level Start AND [NOT SSO Sump Level LIT1802 Failed AND NOT LSO Sump Level LIT1502 Backup High Level Start]) | Penstock Failed OR Penstock Local OR (LSO Level LIT1802 High Level Start OR [SSO Sump Level LIT1802 Failed AND LSO Sump Level LIT1502 Backup High Level Start]) |  |
| S.Silva | Storm Overflow Screens M901-M902 | Storm Overflow Screen Healthy & ([LIT902 Healthy & LIT902 High Level Start] OR Run-On Time NOT Elapsed OR LIT902 Failed OR 24 Hour Run) | Storm Overflow Screen Failed OR (LIT902 Healthy & LIT902 High Level Stop) OR Run-On Time Elapsed | Run Simultaneously |

- ABNORMAL AUTOMATIC OPERATION

| Signature | Failure/Abnormal Condition | Resultant Control Action | Reset Method |
| --- | --- | --- | --- |
|  | Power Failure | All Screens will immediately stop. | Restoration of mains supply. |
|  | PLC Watchdog Fail | All Screens will immediately stop. | Auto control resumes upon PLC being healthy. |
|  | Level LIT902 LOE | Run Storm Screens Continuous | Auto reset once cleared |

- BACK UP CONTROL – PROCESS

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- BACK UP CONTROL – SAFETY

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- MANUAL CONTROL

| Signature | Plant | Selection | Actions |
| --- | --- | --- | --- |
|  | Regulating penstock – RP0001 | Enable when switch selected to hand | Open/Close via push buttons |
|  | Emergency penstock - EP2 | Enable when switch selected to hand | Open/Close via push buttons |

- SUPERVISORY CONTROL

| Signature | Setpoint Group | Setpoint | Comment |
| --- | --- | --- | --- |
|  | Regulating – Penstock RP0001 | Nudge and wait |  |
|  | Storm Overflow Screens | High Level Start |  |
|  | EP2 Control | High Level Start |  |
|  | ODC 1 & 3 | Duty Selection |  |
|  | ODC 2 & 4 | Duty Selection |  |

- TELEMETRY DATA

Nomenclature to be finalised within TagDB. Full configuration to be recorded in accordance with DCWW Document ES404.

| Signature | Name | Type | Priority | Comment |
| --- | --- | --- | --- | --- |
|  | TBC with Storm Tank Upgrade |  |  |  |

- MISCALLANEOUS

<insert anything here deemed useful but not applicable to sections above>

- COMMENTS

| Name | Company | Role | Date | Signature |
| --- | --- | --- | --- | --- |

| ###### Transfer PS |  |
| --- | --- |
| Status | FDS |

- PROCESS OVERVIEW

There are three Transfer Pumps (VSD’s rated at 250 – 400 l/s). These are used to pump the normal outlet flow to Cog Moors WwTW. The maximum flow is limited to 820 l/s. The pumps are run in a duty/assist/standby arrangement. The speed of the pumps is essentially proportional to the Transfer Sump level.

- PLANT OVERVIEW

| Signature | Description | Type | Location | Purpose | Qty | Control System Interface |
| --- | --- | --- | --- | --- | --- | --- |
|  | Pumps – P201/202/203 | VSD | Transfer Sump | Pump Normal flow to Cog Moors WwTW | 3 | Discrete I/O to PLC |
|  | Level – LIT200 | Ultrasonic | Transfer Sump | Measure Level of Sump for pump control | 1 | Discrete I/O to PLC |
|  | Float – LS201 | Float Switch | Transfer Sump | Backup Control | 1 | Discrete I/O to PLC |
|  | Flow Meter – FIT200 | Magnetic Flow Meter | Outlet of Transfer Pumps | Flow Monitoring | 1 | Discrete I/O to PLC |

- CONTROL PHILOSOPHY

Start/Stop Conditions The duty pump is called to run once the “Transfer Sump” level (LIT200) is above the “Transfer Sump High – Start Duty Pump” (adjustable) setpoint for x seconds. If the level then drops below the “Transfer Sump Low Level – Stop Duty Pump” (adjustable) setpoint for x seconds then the pump will stop. The assist pump is called to run once the “Transfer Sump” level (LIT200) is above the “Transfer Sump High – Start Assist Pump” (adjustable) setpoint for x seconds. If the level then drops below the “Transfer Sump Low Level – Stop Assist Pump” (adjustable) setpoint for x seconds then the pump will stop. Speed Control Once the duty pump is called to run it will run at a pre-set speed of 100% (adjustable). Once running at this speed for a pre-set time of 15 minutes (adjustable), then the speed will be increased and decreased via a Linear Level Control loop (adjustable setpoints – higher pump speed at higher level, lower pump speed at lower level to minimise pump starts/hour). Once an assist pump is called to run then all pumps will run at a pre-set speed of 100% (adjustable). Once running at this speed for a pre-set time of 15 minutes (adjustable), then the speed will be increased and decreased via a Linear Level Control loop (adjustable setpoints – higher pump speed at higher level, lower pump speed at lower level to minimise pump starts/hour). Backup Control On a level instrument failure, the pumps will be started/stopped by the float switch as follows: If the float switch (LS201) is activated, then the duty pump will run (at its minimum speed) until X minutes (adjustable) after the float switch is de-activated. If after x minute the float switch is still active or has re-activated and the duty pump is running, then the assist pump is started. Both pumps shall run at minimum speed until X minutes after the float switch has de-activated Flow Limit Control Limits the flow to Cog Moors SWK to not breach existing permits. Setpoint adjustable maximum value that feeds in to the Linear Control loop. This control is ONLY activated by the following: Once TWO pumps are running in auto for x seconds. This control is de-activated by the following: One or NO pumps are running in auto for x seconds.

- NORMAL AUTOMATIC OPERATION

| Signature | Drive | Enabler(s) | Disabler(s) | Modifier(s) |
| --- | --- | --- | --- | --- |
| S. Silva | Duty Transfer Pump | (Mains Healthy OR [Mains Failed & Generator Power Available & Gen Available for Transfer Pumps]) & (Transfer Sump LIT200 Duty High Level Start Reached OR [Transfer Sump LIT200 Failed & Transfer Sump Float Duty Start Level Reached]) & Transfer Pump Healthy | (Mains Failed & Generator Power Unavailable & Gen Unavailable for Transfer Pumps) OR Transfer Sump LIT200 Duty High Level Stop Reached OR (Transfer Sump LIT200 Healthy & NOT Transfer Sump Float Start Level Reached) OR Transfer Pump Failed | - Start-Up Speed Fixed (adjustable) for Set Time (adjustable) - Linear Level Control - Flow Limit Control Trimming PID Max Output for Speed |
| S.Silva | Assist Transfer Pump | (Mains Healthy OR [Mains Failed & Generator Power Available & Gen Available for Transfer Pumps]) & (Transfer Sump LIT200 Assist High Level Start Reached OR [Transfer Sump LIT200 Failed & Transfer Sump Float Assist Start Level Reached]) & Transfer Pump Healthy | (Mains Failed & Generator Power Unavailable & Gen Unavailable for Transfer Pumps) OR Transfer Sump LIT200 Assist High Level Stop Reached OR (Transfer Sump LIT200 Healthy & NOT Transfer Sump Float Assist Start Level Reached) OR Transfer Pump Failed | - Start-Up Speed Fixed (adjustable) for Set Time (adjustable) - Linear Level Control - Flow Limit Control Trimming PID Max Output for Speed |

- ABNORMAL AUTOMATIC OPERATION

| Signature | Failure/Abnormal Condition | Resultant Control Action | Reset Method |
| --- | --- | --- | --- |
|  | Power Failure | All Transfer Pumps will immediately stop and be controlled via local level controller relays | Restoration of mains supply |
|  | PLC Watchdog Fail | All Transfer pumps will immediately stop | Auto control resumes upon PLC being healthy |
|  | HMI-PLC network comms fail | No effect on automatic operation of pumps. Loss of supervisory control and local alarm monitoring | Auto resume when network comms restored |
|  | Pump Failed | Immediately stop associated pump Duty changeover (To standby else next available assist) | Auto reset once cleared at associated starter via reset button Duty regime will also reinstate original pump if still duty. |
|  | Pump Trip | Immediately stop associated pump Duty changeover (To standby, else next available assist) | Reset on HMI to clear E-Stop alarm and Auto control will resume. Duty regime will also reinstate original pump if still duty. |
|  | LIT200 LOE | Pumps will go into Backup control mode | Auto resume normal operation when LIT200 is healthy |

- BACK UP CONTROL – PROCESS

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |
|  | Transfer Sump Level > SP | High Flow | Start Duty Gen in prep for SSO Pumps |
|  | Float Switch LS201 | Once activated, Duty pump will run at minimum speed for an adjustable time after the float is de-activated. Assist will start after 1 minute of float switch still activated | Normal operation will resume when LIT200 is healthy |

- BACK UP CONTROL – SAFETY

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- MANUAL CONTROL

| Signature | Plant | Selection | Actions |
| --- | --- | --- | --- |
|  | Transfer Pumps | Enable when starter selector switch selected to hand | Start/Stop via push buttons |

- SUPERVISORY CONTROL

| Signature | Setpoint Group | Setpoint | Comment |
| --- | --- | --- | --- |
|  | Transfer Pumps | Duty Control Duty High Level Start/Stop Assist High Level Start/Stop Pump Speed – Duty Linear Control Pump Speed – Assist Linear Control Startup Timer Startup Speed Backup Float - Control Flow Limit - PID |  |

- TELEMETRY DATA

Nomenclature to be finalised within TagDB. Full configuration to be recorded in accordance with DCWW Document ES404.

| Signature | Name | Type | Priority | Comment |
| --- | --- | --- | --- | --- |
|  | TBC with Storm Tank Upgrade |  |  |  |

- MISCALLANEOUS

<insert anything here deemed useful but not applicable to sections above>

- COMMENTS

| Name | Company | Role | Date | Signature |
| --- | --- | --- | --- | --- |

| ###### Long Sea Outfall PS |  |
| --- | --- |
| Status | FDS |

- PROCESS OVERVIEW

There are three Long Sea Outfall Pumps (VSD’s rated at 250 – 400 l/s). These pumps are used when the Transfer Pumps cannot cope with the flow and are used as Duty / Assist-Standby / Assist-Standby There is a Penstock that allows flow in to the LSO Sump when there is an increased flow through site to ensure it does not flood.

- PLANT OVERVIEW

| Signature | Description | Type | Location | Purpose | Qty | Control System Interface |
| --- | --- | --- | --- | --- | --- | --- |
|  | LSO Pumps – P1501/P1502/P1503 | VSD | Overflow from Transfer Sump | Pump Flows out that transfer station cannot cope with | 3 | Discrete I/O to PLC |
|  | Level – LIT1502 | Ultrasonic | LSO Sump | Measure Level | 1 | Discrete I/O to PLC |
|  | Pressure – PIT2204 | Pressure | LSO Pump Outlet | Measure Deliver Pressure | 1 | Discrete I/O to PLC |
|  | LSO Sump Valve – AV1520 | Electrically Actuated Penstock | LSO Outlet | Allow flow into LSO Sump | 1 | Discrete I/O to PLC |

- CONTROL PHILOSOPHY

Linking with SSO Pumps and Storm Tank Filling Because there is a hydraulic link between the LSO and the SSO Sump, the LSO pumps will initially attempt to relieve the site of any excess flow by utilising the ‘Barry Trickle’. This is where 1 LSO pump runs at a fixed speed that correlates with the Barry Trickle consent flow. Once the level in the SSO Sump reaches the high level start setpoint then the LSO pump will stop and 1 SSO Pump will run to fill the storm tank, providing the storm tank outlet valve is closed, the storm tank inlet valve is open and it’s not inhibited from the storm tank PLC. Once the storm tank has filled, the SSO pump will stop to allow the storm tank inlet valve to close. Once the closed feedback has been received, the SSO pumps will continue to run in a Duty/Assist1/Assist2 arrangement to relieve Barry West SPS of incoming flows. If the site maintains to struggle with high flows, then the LSO pumps will restart in a Duty/Assist1/Assist2 arrangement until the flows and levels settle down. Start/Stop Conditions The Duty pump is called to run when the level (LIT1502) is above the duty start level set point (adjustable) for a preset time (Adjustable). The Duty pump will stop when the level (LIT1502) is below the duty start level set point (adjustable) for a preset time (Adjustable). The Assist pump is called to run when the level (LIT1502) is above the Assist start level set point (adjustable) for a preset time (Adjustable) and the LSO Sump Valve is open. The Assist pump will stop when the level (LIT1502) is below the Assist start level set point (adjustable) for a preset time (Adjustable) or the LSO Sump Valve is closed. The 2nd Assist pump is called to run when the level (LIT1502) is above the Assist 2 start level set point (adjustable) for a preset time (Adjustable) and the LSO Sump Valve is open. The 2nd Assist pump will stop when the level (LIT1502) is below the Assist 2 start level set point (adjustable) for a preset time (Adjustable) or the LSO Sump Valve is closed. Delivery Pressure If the pressure exceeds the “High Delivery Pressure” setpoint for X seconds, then an alarm will be raised. If the pressure exceeds the “High-High Delivery Pressure” setpoint for X seconds then an alarm will be raised. Also, the pumps will be called to stop. This will require a reset. Speed Control When in Barry Trickle mode (Singular LSO Pump Running and LSO Sump Valve is closed) a singular pump will run at a HMI adjustable speed (aligning with max. flow for Barry Trickle). Once a second or third pump is called to run and the LSO Sump Valve is open, the speed will ramp up to a HMI adjustable speed and stay there until only one or no pump is required. Power LSO pumps run off mains supply and if mains supply fails then LSO pumps can be run from generators, if sufficient power is available. If only one generator is available, then the LSO pumps are inhibited. LSO Sump Valve The LSO Sump Valve ensures the site can be relieved by filling the LSO Sump to enable the pumps to run. If both the Storm Tank Inlet and Outlet Valve are Closed and the LIT1802 (SSO) High Level Adjustable Setpoint has been reached then the Valve will open. There is also a maintenance cycle on the LSO Sump Valve to cycle it every 24hrs permitting the Storm Screens aren’t running in auto.

- NORMAL AUTOMATIC OPERATION

| Signature | Drive | Enabler(s) | Disabler(s) | Modifier(s) |
| --- | --- | --- | --- | --- |
| S.Silva | Duty LSO Pump | Duty Pump Healthy & Duty Start Level Reached & (Mains Healthy OR [Mains Failed & Generator Available for Mains & NOT One Genny Avail – Inhibit All Foul Pumps & NOT No Power for Fouls And Assist Transfer Pumps]) | Duty Pump Failed OR Duty Stop Level Reached OR Power Interlock as per the enablers | - Adjustable ‘Barry Trickle’ Speed Setpoint for single pump running. |
| S.Silva | Assist 1 LSO Pump | Assist 1 Pump Healthy & Assist 1 Start Level Reached & LSO Sump Valve Opened & Power Healthy as per above | Assist 1 Pump Failed OR Assist 1 Stop Level Reached OR LSO Sump Valve Closed OR Power Interlock | - Adjustable Fixed Speed Setpoint for multiple pumps running. |
| S.Silva | Assist 2 LSO Pump | Assist 2 Pump Healthy & Assist 2 Start Level Reached & LSO Sump Valve Opened & Power Healthy | Assist 2 Pump Failed OR Assist 2 Stop Level Reached OR LSO Sump Valve Closed OR Power Interlock | - Adjustable Fixed Speed Setpoint for multiple pumps running. |
| S. Silva | LSO Sump Valve | Penstock Healthy & LIT1802 Healthy & LIT1802 Open Level Reached & Storm Tank Inlet Valve Closed & Storm Tank Outlet Valve Closed | Penstock Failed OR LIT1802 Failed OR LIT1802 Closed Level Reached OR Storm Tank Inlet Valve NOT Closed OR Storm Tank Outlet Valve NOT Closed |  |

- ABNORMAL AUTOMATIC OPERATION

| Signature | Failure/Abnormal Condition | Resultant Control Action | Reset Method |
| --- | --- | --- | --- |
|  | Power Failure | All LSO Pumps will immediately stop. UPS will maintain PLC supply for a minimum of 30 Minutes. | Restoration of mains supply. |
|  | PLC Watchdog Fail | All LSO pumps will immediately stop | Auto control resumes upon PLC being healthy. |
|  | HMI-PLC network comms fail | No effect on automatic operation of pumps. Loss of supervisory control and local alarm monitoring. | Auto resume when network comms restored. |
|  | Pump Trip | Remove run signal and start next assist/standby pump. | Pump will continue once reset and healthy. |
|  | Delivery pressure high | Inhibit pumps. | Auto reset once cleared and pumps will continue. |
|  | Level – LIT1502 Failed/OOR | Stop all LSO Pumps. | Auto reset when Level is healthy. |
|  | Mains Failed | Generator to supply power but LSO will be inhibited if only 1 generator is available. | Normal operation will resume when mains is restored or multiple generators are available. |

- BACK UP CONTROL – PROCESS

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- BACK UP CONTROL – SAFETY

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- MANUAL CONTROL

| Signature | Plant | Selection | Actions |
| --- | --- | --- | --- |
|  | LSO Pumps | Enable when starter selector switch selected to hand | Start/Stop via push buttons |
|  | LSO Sump Valve | Enable when selector switch selected to hand | Open/Close via push buttons |

- SUPERVISORY CONTROL

| Signature | Setpoint Group | Setpoint | Comment |
| --- | --- | --- | --- |
|  | LSO Pumps | Duty Control Duty High Level Start Assist 1 High Level Start Assist 2 High Level Start Stopped Timer (If Pumps Stopped for setpoint adjustable time period then send Storm Tank PLC ‘LSO Stopped’ signal) Barry Trickle Speed Pump Speed |  |
|  | LSO Sump Valve | High Level Open |  |
|  | Level LIT1502 | SSO Pumps Enable Backup Level Start |  |

- TELEMETRY DATA

Nomenclature to be finalised within TagDB. Full configuration to be recorded in accordance with DCWW Document ES404.

| Signature | Name | Type | Priority | Comment |
| --- | --- | --- | --- | --- |
|  | TBC with Storm Tank Upgrade |  |  |  |

- MISCALLANEOUS

<insert anything here deemed useful but not applicable to sections above>

- COMMENTS

| Name | Company | Role | Date | Signature |
| --- | --- | --- | --- | --- |

| ###### Short Sea Outfall PS |  |
| --- | --- |
| Status | FDS |

- PROCESS OVERVIEW

These four fixed speed pumps are used in storm conditions to pump flow into the Storm Tank, when these are full they will pump out to the Short Sea Outfall. These pumps are used when the Transfer and LSO Pumps cannot cope with the flow and are used as Duty / Assist1 / Assist2 / Standby

- PLANT OVERVIEW

| Signature | Description | Type | Location | Purpose | Qty | Control System Interface |
| --- | --- | --- | --- | --- | --- | --- |
|  | Short Sea Outfall Pumps (SSO) – P1801/P1802/P1803/P1804 | Soft-Start (Fixed Speed) | SSO Sump | Pump to Storm tanks when LSO cannot cope and then Short Sea Outfall when Storm Tank is full. | 4 | Discrete I/O to PLC |
|  | Level – LIT1802 | Ultrasonic | SSO Sump | Measure SSO Level. | 1 | Discrete I/O to PLC |
|  | SSO Sump Pump P1800 | DOL (Fixed Speed) | SSO Sump | Pump remaining level in SSO Sump. | 1 | Discrete I/O to PLC |

- CONTROL PHILOSOPHY

Linking with LSO Pumps and Storm Tank Filling Because there is a hydraulic link between the LSO and the SSO Sump, the LSO pumps will initially attempt to relieve the site of any excess flow by utilising the ‘Barry Trickle’. This is where 1 LSO pump runs at a fixed speed that correlates with the Barry Trickle consent flow. Once the level in the SSO Sump reaches the high level start setpoint then the LSO pump will stop and 1 SSO Pump will run to fill the storm tank, providing the storm tank outlet valve is closed, the storm tank inlet valve is open and it’s not inhibited from the storm tank PLC. Once the storm tank has filled, the SSO pump will stop to allow the storm tank inlet valve to close. Once the closed feedback has been received, the SSO pumps will continue to run in a Duty/Assist1/Assist2 arrangement to relieve Barry West SPS of incoming flows. If the site maintains to struggle with high flows, then the LSO pumps will restart in a Duty/Assist1/Assist2 arrangement until the flows and levels settle down. Start/Stop Conditions The Duty Pump will be called to run in 3 instances: - The Storm Tank Inlet Valve is Open, the Storm Tank Outlet Valve is Closed, the Storm Tank PLC is NOT inhibiting the SSO Pump from running and the High Level Start Setpoint has been reached in the SSO Sump. - 3 LSO Pumps are running and the LSO High Level Start has been reached. - The SSO High Level and LSO High Level Start Setpoints have been reached. The assist pump will be called to run when the SSO Level (LIT1802) is above the assist start setpoint for a pre-set time and the Duty SSO Pump is running. The Assist pump will stop when the SSO Level (LIT1802) is below the assist stop setpoint for a pre-set time or if the Duty SSO Pump is stopped. The 2nd assist pump will be called to run when the SSO Level (LIT1802) is above the assist 2 start setpoint for a pre-set time and the Duty and Assist Pumps are running. The 2nd Assist pump will stop when the SSO Level (LIT1802) is below the assist 2 stop setpoint for a pre-set time or the Duty or Assist Pump has stopped. Power The SSO pumps only run on generator power. Each pump will be called to run once a generator has started and is available. Each SSO pump requires a generator to run. SSO Sump Pump There is an SSO Sump Pump to drain the SSO Sump from any level that can’t be pumped away due to the height of the suction side of each pump. Providing no SSO or LSO Pumps are running, the Transfer Sump is not High Level, the Storm Screens are not running and the Sump Pump High Level Start Setpoint has been reached the SSO Sump Pump can run until its Stop Level.

- NORMAL AUTOMATIC OPERATION

| Signature | Drive | Enabler(s) | Disabler(s) | Modifier(s) |
| --- | --- | --- | --- | --- |
| S.Silva | Duty SSO Pump | Duty Generator Available for Storm & Duty Pump Healthy & ([Duty Pump High Level Start & Storm Tank Inlet Valve Opened & Storm Tank Outlet Valve Closed & SSO NOT Inhibited from Storm Tank PLC] OR [3 LSO Pumps Running & LSO High Level Start] OR [Duty Pump High Level Start & LSO High Level Start]) | Duty Generator NOT Available for Storm OR Duty Pump Unavailable OR (Duty Pump Low Level Stop OR Storm Tank Inlet Valve Closed OR Storm Tank Outlet Valve Open OR SSO Inhibited from Storm Tank PLC) OR (< 3 LSO Pumps Running OR LSO Low Level Stop) OR (Duty Pump Low Level Stop OR LSO Low Level Stop) |  |
| S.Silva | Assist 1 SSO Pump | Assist 1 Generator Available for Storm & Assist 1 Pump Healthy & Duty Pump Running & Assist 1 Pump High Level Start | Assist 1 Generator NOT Available for Storm OR Assist 1 Pump Unavailable OR Duty Pump Stopped OR Assist 1 Pump Low Level Stop |  |
| S.Silva | Assist 2 SSO Pump | Assist 2 Generator Available for Storm & Assist 2 Pump Healthy & Duty and Assist 1 Pump Running & Assist 2 Pump High Level Start | Assist 2 Generator NOT Available for Storm OR Assist 2 Pump Unavailable OR Duty OR Assist 1 Pump Stopped OR Assist 2 Pump Low Level Stop |  |
| S.Silva | SSO Sump Pump | No LSO & SSO Pumps Running & Transfer Sump LIT200 NOT High Level & Storm Screens Stopped & Sump Pump High Level Start | Any LSO & SSO Pumps Running & Transfer Sump LIT200 High Level & Storm Screens Running & Sump Pump Low Level Stop |  |

- ABNORMAL AUTOMATIC OPERATION

| Signature | Failure/Abnormal Condition | Resultant Control Action | Reset Method |
| --- | --- | --- | --- |
|  | Generator Power Failure | All SSO Pumps will immediately stop. | Reinstate power. |
|  | PLC Watchdog Fail | All SSO pumps will immediately stop. | Auto control resumes upon PLC being healthy. |
|  | HMI-PLC network comms fail | No effect on automatic operation of pumps. Loss of supervisory control and local alarm monitoring. | Auto resume when network comms restored. |
|  | Pump Tripped | Remove run signal and start next assist pump. | Resume normal operation when pump is reset and healthy. |
|  | Level LIT1802 LOE/OOR | Stop SSO Pumps if running off of LIT1802. | Auto resume when level is healthy. |
|  | Storm Tank Inlet Penstock failed Mid Travel | Stop SSO Pumps. | Auto resume when penstocks are open or close. |
|  | Storm Tank Outlet Penstock Failed Mid travel | Stop SSO Pumps. | Auto resume when penstocks are open or close. |

- BACK UP CONTROL – PROCESS

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- BACK UP CONTROL – SAFETY

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- MANUAL CONTROL

| Signature | Plant | Selection | Actions |
| --- | --- | --- | --- |
|  | SSO Pumps | Enable when starter selector switch selected to hand. | Start/Stop via push buttons. |
|  | SSO Sump Pump | Enable when starter selector switch selected to hand. | Start/Stop via push buttons. |
| - SUPERVISORY CONTROL |  |  |  |

| Signature | Setpoint Group | Setpoint | Comment |
| --- | --- | --- | --- |
|  | SSO Pumps | Duty Control Duty High Level Start Assist 1 High Level Start Assist 2 High Level Start SSO Stopped Timer |  |
|  | SSO Sump Pump | SSO Sump Pump High Level Start |  |

- TELEMETRY DATA

Nomenclature to be finalised within TagDB. Full configuration to be recorded in accordance with DCWW Document ES404.

| Signature | Name | Type | Priority | Comment |
| --- | --- | --- | --- | --- |
|  | TBC with Storm Tank Upgrade |  |  |  |

- MISCALLANEOUS

<insert anything here deemed useful but not applicable to sections above>

- COMMENTS

| Name | Company | Role | Date | Signature |
| --- | --- | --- | --- | --- |

| ###### Storm Tank |  |
| --- | --- |
| Status | FDS |

- PROCESS OVERVIEW

A Mitsubishi FX PLC controls the Storm Tank equipment, however, this PLC is used to send commands to assist in the control.

- PLANT OVERVIEW

| Signature | Description | Type | Location | Purpose | Qty | Control System Interface |
| --- | --- | --- | --- | --- | --- | --- |
|  | Storm Tank Outlet Valve - MV2002 | Electrically Actuated Valve | Outlet of Storm tank | Drain Storm Tank | 1 | Discrete I/O from FX PLX |
|  | Storm Tank inlet Valve – MV2001 | Electrically Actuated Valve | Inlet of Storm Tank | Allows Storm Tank to Fill and Isolate | 1 | Discrete I/O from FX PLX |
|  | Re-Suspension pump – P2001 | DOL (Fixed Speed) | Storm Tank | Mix Storm Tank | 1 | Discrete I/O from FX PLX |
|  | Storm Tank Float Switch – LS2001 | Float switch | Storm Tank | High Level Switch | 1 | Discrete I/O from FX PLX |
|  | Storm Tank Level – LIT2001 | Ultrasonic | Storm Tank | Monitor Level in Storm Tank | 1 | Discrete I/O from FX PLX |

- CONTROL PHILOSOPHY

SSO Level Start Required (SSOPmp_Level in Storm PLC) Constantly enabled via: NOT LOE LIT1802 AND NOT OOR LIT1802. No SSO Pumps Running (SSOPmp_Stopped in Storm PLC) SSO Pump 1 NOT Running AND SSO Pump 2 NOT Running AND SSO Pump 3 NOT Running AND SSO Pump 4 NOT Running Permit to Drain Storm Tank – Inlet Flume Permit Level (MW_LSOHlthy In Storm PLC) FIT1202 Low Level Set AND NOT FIT1202 High Level Set AND NOT OOR FIT1202 AND NOT LOE FIT1202 AND NOT SSO/LSO Pumps Running The below information contains the signals in the Storm Tank PLC, this is informative and won’t be amended. Storm Tank Inlet Valve Open Conditions Once selected to “Auto” the valve will open on the following condition: The Storm Tank is NOT full (generated within the Storm Tank PLC). AND The Storm Tank level is healthy (generated within the Storm Tank PLC). AND The duty SSO Pump has been “Called To Run” in auto. Storm Tank Inlet will be closed as follows: The Storm Tank is full (generated within the Storm Tank PLC). OR The Storm Tank float switch is activated (generated within the Storm Tank PLC). OR The Storm Tank level is NOT healthy (generated within the Storm Tank PLC). OR The Storm Tank PLC has failed (generated within the Storm Tank PLC). OR The Storm Tank ICA supply is NOT healthy (generated within the Storm Tank PLC). OR ALL SSO Pumps are stopped. Note: Once the valve has closed on a “Tank Full” condition i.e. full level reached or float activated then the valve will NOT re-open until the Storm Tank Level is below the “Storm Tank Low Level – Re-Open Inlet Valve” setpoint. Storm Tank Outlet Valve Open / Close Conditions Once selected to “Auto” the valve will open on the following condition: The Storm Tank Inlet Valve IS closed (generated within the Storm Tank PLC). AND The Storm Tank is NOT empty (generated within the Storm Tank PLC). AND ALL SSO Pumps have stopped for more than 30 minutes (adjustable). AND ALL LSO Pumps have stopped for more than 30 minutes (adjustable). AND The Inlet Flume Level Flow is below 700l/s for 20 minutes (adjustable). The valve will be closed as follows: The Storm Tank level has fallen below a low setpoint for 10 minutes (generated within the Storm Tank PLC). OR The Storm Tank level is NOT healthy (generated within the Storm Tank PLC). OR The Storm Tank PLC has failed (generated within the Storm Tank PLC). OR ANY LSO Pumps are running in auto. OR ANY SSO Pumps are running in auto. OR The Inlet Flume Level Flow is above 780l/s for 20 minutes (adjustable).

- NORMAL AUTOMATIC OPERATION

| Signature | Drive | Enabler(s) | Disabler(s) | Modifier(s) |
| --- | --- | --- | --- | --- |
| S.Silva | SSO Level Start Required | NOT LOE LIT1802 & NOT OOR LIT1802 | LOE LIT1802 OR OOR LIT1802 |  |
| S.Silva | No SSO Pumps Running | SSO Pump 1 NOT Running & SSO Pump 2 NOT Running & SSO Pump 3 NOT Running & SSO Pump 4 NOT Running & LSO Pump 1 NOT Running & LSO Pump 2 NOT Running & LSO Pump 3 NOT Running | SSO Pump 1 Running OR SSO Pump 2 Running OR SSO Pump 3 Running OR SSO Pump 4 Running OR LSO Pump 1 Running OR LSO Pump 2 Running OR LSO Pump 3 Running |  |
| S.Silva | Permit to Drain Storm Tank – Inlet Flume Permit Level | FIT1202 Low Level Set & NOT FIT1202 High Level Set & NOT OOR FIT1202 & NOT LOE FIT1202 & NOT SSO/LSO Pumps Running | NOT FIT1202 Low Level Set OR FIT1202 High Level Set OR OOR FIT1202 OR LOE FIT1202 OR SSO/LSO Pumps Running |  |

- ABNORMAL AUTOMATIC OPERATION

| Signature | Failure/Abnormal Condition | Resultant Control Action | Reset Method |
| --- | --- | --- | --- |
|  | Mains Failure | Close Both Inlet and outlet Valves | Restoration of mains supply |
|  | PLC Watchdog Fail | Close Both Inlet and outlet Valves | Auto control resumes upon PLC being healthy |
|  | HMI-PLC network comms fail | No effect on automatic operation. Loss of supervisory control and local alarm monitoring | Auto resume when network comms restored |

- BACK UP CONTROL – PROCESS

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- BACK UP CONTROL – SAFETY

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- MANUAL CONTROL

| Signature | Plant | Selection | Actions |
| --- | --- | --- | --- |
|  | Storm tank inlet valve | Enable when started selector switch selected to hand | Open/Close via push buttons |
|  | Storm tank outlet valve | Enable when started selector switch selected to hand | Open/Close via push buttons |
| - SUPERVISORY CONTROL |  |  |  |

| Signature | Setpoint Group | Setpoint | Comment |
| --- | --- | --- | --- |
|  | Inlet Flow | Low Level Start |  |
|  | SSO Pumps | Stop Time | As per SSO Section |
|  | LSO Pumps | Stop Time | As per LSO Section |

- TELEMETRY DATA

Nomenclature to be finalised within TagDB. Full configuration to be recorded in accordance with DCWW Document ES404.

| Signature | Name | Type | Priority | Comment |
| --- | --- | --- | --- | --- |
|  | TBC with Storm Tank Upgrade |  |  |  |

- MISCALLANEOUS

<insert anything here deemed useful but not applicable to sections above>

- COMMENTS

| Name | Company | Role | Date | Signature |
| --- | --- | --- | --- | --- |

| ###### Odour Control |  |
| --- | --- |
| Status | FDS |

- PROCESS OVERVIEW

There are 4 Odour Control Fans on site, which are grouped in two as Duty/Standby.

- PLANT OVERVIEW

| Signature | Description | Type | Location | Purpose | Qty | Control System Interface |
| --- | --- | --- | --- | --- | --- | --- |
|  | Odour Fans (M3001, 2, 3 & 4) | DOL | Outside Main Compound | Minimise Odour on site. | 4 | Discrete I/O. |

- CONTROL PHILOSOPHY

Odour Control Fans There are two groups of fans, labelled as 1&3 and 2&4. These operate on a Duty/Standby arrangement within the group. When the fan is healthy, duty and not interlocked, it will run. Or if the standby fan is called to run and is not available.

- NORMAL AUTOMATIC OPERATION

| Signature | Drive | Enabler(s) | Disabler(s) | Modifier(s) |
| --- | --- | --- | --- | --- |
| S. Silva | Odour Fans (M3001, 2, 3 & 4) | Odour Fan Healthy & (Odour Fan Duty OR [Odour Fan Standby & Duty Odour Fan Not Available]) & Odour Fan NOT Interlocked | Odour Fan Failed OR Odour Fan Interlocked |  |

- ABNORMAL AUTOMATIC OPERATION

| Signature | Failure/Abnormal Condition | Resultant Control Action | Reset Method |
| --- | --- | --- | --- |

- BACK UP CONTROL – PROCESS

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- BACK UP CONTROL – SAFETY

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- MANUAL CONTROL

| Signature | Plant | Selection | Actions |
| --- | --- | --- | --- |
|  | Odour Fans (M3001, 2, 3 & 4) | Enable when starter selector switch selected to hand. | Start/Stop on panel. |
| - SUPERVISORY CONTROL |  |  |  |

| Signature | Setpoint Group | Setpoint | Comment |
| --- | --- | --- | --- |
|  | Odour Fans (M3001, 2, 3 & 4) | Duty Control |  |

- TELEMETRY DATA

Nomenclature to be finalised within TagDB. Full configuration to be recorded in accordance with DCWW Document ES404.

| Signature | Name | Type | Priority | Comment |
| --- | --- | --- | --- | --- |
|  | TBC with Storm Tank Upgrade |  |  |  |

- MISCALLANEOUS

<insert anything here deemed useful but not applicable to sections above>

- COMMENTS

| Name | Company | Role | Date | Signature |
| --- | --- | --- | --- | --- |
| Sebastian Silva | DCWW | OT Analyst | 07/05/2024 | S. Silva |
| Odour Fans 2 & 4 have been included for future refurbishments; however, these are currently locked off on site. |  |  |  |  |

| ###### Site Power Control |  |
| --- | --- |
| Status | FDS |

- PROCESS OVERVIEW

Due to the supply on site, Barry West SPS cannot have certain items start at once. This will increase risk of overloading the mains. As a result, a staggered start approach is undertaken to limit any issues and the site is supported by generators. The latter will run when certain pumps are called to run too. This chapter captures the workings of the generators and the staggered start.

- PLANT OVERVIEW

| Signature | Description | Type | Location | Purpose | Qty | Control System Interface |
| --- | --- | --- | --- | --- | --- | --- |
|  | Generator 1, 2 & 3 | Diesel Generator | Generator Room | Support power supply on site. | 3 | Discrete I/O. |

- CONTROL PHILOSOPHY

Staggered Start Sequence Staggered Start 1 If the start sequence isn’t being reset, it will activate the timer for Staggered Start 1. The time is a preset value in the PLC. Staggered Start 2 – 15 These bits will energise when the previous fixed timers elapse. Generator Control The generators on site will take over the site mains in case they fail and will assist the mains when the load exceeds site supply. There are 3 generators and 3 tasks that will start either 1, 2 or 3 generators. 2 generators will run on mains failure or 3 if an assist OR 2nd assist SSO Pump, assist or 2nd assist Island Storm Pump is requested. Task A (Request to run 1 generator) If a duty SSO Pump or a duty and assist SSO Pump is/are requested to run, a duty Island Storm Pump is requested to run, the Transfer Sump (LIT200) reaches overflow level, LIT902 reaches a high level or LIT902 is failed or out of range, or the generator has been manually requested to start, Task A will be enabled. Task B (Request to run 2nd generator) If an assist or 2nd assist SSO Pump is required to run, an assist Island Storm Pump is required to run or two generators are requested to run manually, Task B will be enabled. Task C (Request to run 3rd generator) To enable Task C, a 2nd assist SSO pump is required to run, a 2nd assist Island Storm Pump is required to run, or three generators are requested to run manually.

- NORMAL AUTOMATIC OPERATION

| Signature | Drive | Enabler(s) | Disabler(s) | Modifier(s) |
| --- | --- | --- | --- | --- |
|  | Duty Generator | Mains Failure OR Duty SSO Pump Run Request OR (Duty SSO & Assist SSO Pump Run Request) OR Duty Island Storm Pump Run Request OR Transfer Sump (LIT200) Overflow High Level Start OR LIT902 High Level Start OR LIT902 OOR OR LIT902 Failed | Main Healthy OR Duty SSO Pump NOT Run Requested & (Duty SSO & Assist SSO Pump NOT Run Request) & Duty Island Storm Pump NOT Run Request & Transfer Sump (LIT200) Overflow High Level Stop & LIT902 High Level Stop & LIT902 NOT OOR & LIT902 Healthy |  |
|  | 1st Assist Generator | Mains Failure OR Assist SSO Pump Run Request OR (1st Assist AND 2nd Assist SSO Pump Run Request) OR Assist Island Storm Pump Run Request | Mains Healthy & Assist SSO Pump NOT Run Request & (1st Assist & 2nd Assist SSO Pump NOT Run Request) & Assist Island Storm Pump NOT Run Request |  |
|  | 2nd Assist Generator | (Mains Failure & [1st Assist SSO Run Request OR 2nd Assist SSO Run Request OR 1st Assist Island Storm Pump Run Request OR 2nd Assist Island Storm Pump Run Request]) OR 2nd Assist SSO Pump Run Request OR 2nd Assist Island Storm Pump Run Request | (Mains Healthy & [1st Assist SSO NOT Run Request OR 2nd Assist SSO NOT Run Request OR 1st Assist Island Storm Pump NOT Run Request OR 2nd Assist Island Storm Pump NOT Run Request]) & 2nd Assist SSO Pump NOT Run Request & 2nd Assist Island Storm Pump NOT Run Request |  |
|  | Staggered Start 1 | (Mains ACB Open & Generator 1 ACB Open & Generator 2 ACB Open & Generator 3 ACB Open) OR (Mains Healthy & Bus ACB NOT Open) | Mains ACB Closed OR Generator 1 ACB Closed OR Generator 2 ACB Closed OR Generator 3 ACB Closed) OR (Mains Failed OR Bus ACB Open ) |  |
|  | Staggered Start 2-15 | Staggered Start n-1 Delay Timer Elapsed | Staggered Start n-1 Delay Timer NOT Elapsed |  |
|  | Generator Power Available for Mains | One Generator Running |  |  |
|  | Generator Power Available for Duty Storm | One Generator Run Request & 2 or More Generators Available for Mains |  |  |
|  | Generator Power Available for 1st Assist Storm | (2 Generators Run Request & 2 Generators Running & 3 Generators Available for Mains) OR (One Generator Run Request & One Generator Running & One 2 or More Generators Available for Mains) |  |  |
|  | Generator Power Available for 2nd Assist Storm | (3 Generators Run Request & 3 Generators Running & NOT 3 Generators Power Available for Mains) OR (One Generator Run Request & One Generator Running & NOT One Generator Power Available for Mains) |  |  |
|  | One Genny Available – Inhibit ALL Foul Pumps | Mains Failure & One Generator Running |  |  |
|  | One Genny Available – Inhibit ALL Transfer Pumps | Mains Failure & One Generator Running & (Duty SSO Pump Run Request OR Duty Island Storm Pump Run Request) |  |  |
|  | No Power for Fouls & Assist Transfer Pumps on Generators | 3 Generators Run Request & 2 Generators Failed |  |  |

- ABNORMAL AUTOMATIC OPERATION

| Signature | Failure/Abnormal Condition | Resultant Control Action | Reset Method |
| --- | --- | --- | --- |

- BACK UP CONTROL – PROCESS

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- BACK UP CONTROL – SAFETY

| Signature | Event | Cause | Result |
| --- | --- | --- | --- |

- MANUAL CONTROL

| Signature | Plant | Selection | Actions |
| --- | --- | --- | --- |
|  | Generator 1 | Keyswitch enabled. | Start/Stop on controller. |
|  | Generator 2 | Keyswitch enabled. | Start/Stop on controller. |
|  | Generator 3 | Keyswitch enabled. | Start/Stop on controller. |
| - SUPERVISORY CONTROL |  |  |  |

| Signature | Setpoint Group | Setpoint | Comment |
| --- | --- | --- | --- |
|  | Duty Start Command Button | Start Button |  |
|  | Duty & Assist 1 Start Command Button | Start Button |  |
|  | Duty, Assist 1 & Assist 2 Start Command Button | Start Button |  |

- TELEMETRY DATA

Nomenclature to be finalised within TagDB. Full configuration to be recorded in accordance with DCWW Document ES404.

| Signature | Name | Type | Priority | Comment |
| --- | --- | --- | --- | --- |
|  | TBC with Storm Tank Upgrades |  |  |  |

- MISCALLANEOUS

<insert anything here deemed useful but not applicable to sections above>

- COMMENTS

| Name | Company | Role | Date | Signature |
| --- | --- | --- | --- | --- |