Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	BJ9681IX

	Name of operator
	Essity UK Ltd Oakenholt Mill.

	Location of Facility
	Chester Road, Oakenholt, Flintshire, CH6 5PU

	Time and date of the detection 
	July 23rd, 2019.


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	July 23rd, 2019.

	Reference or description of the location of the event 
	W1

	Description of where any release into the environment took place
	W1

	Substances(s) potentially released
	Water

	Best estimate of the quantity or rate of release of substances
	42.03m3

	Measures taken, or intended to be taken, to stop any emission
	None


	Description of the failure or accident.
	Released out of consent water with high temperature of 29.48 degrees versus permit limit of 25 degrees. 


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	W1

	Parameter(s)
	Water

	Limit
	25 degrees

	Measured value and uncertainty
	29.48

	Date and time of monitoring
	July 23rd, 2019.

	Measures taken, or intended to be taken, to stop the emission
	Lag pipework to protect from high temp from direct sunlight. Put on line 3rd heat exchanger in August site shut. Relocate temperature probe to more suitable location.



	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	W1

	Substances(s) detected
	High temperature water

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	None

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	None

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	Lag pipework to protect from high temp from direct sunlight. Put on line 3rd heat exchanger in August site shut. Relocate temperature probe to more suitable location.



	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	11/07/17, 11/08/17, 17/01/18, 06/03/18, 09/07/18, 24/04/19.


	Name*
	Mike King

	Post
	Safety Specialist & Environmental Leader

	Signature
	

	Date
	25/07/19


* authorised to sign on behalf of the operator



