[image: image1.emf]
OGN 200 Form 1A
Record of a Habitats Regulations Assessment

	Plan or project name, brief description or application reference number
	Application for a new bespoke permit – Hyperscale Data Centre
Application reference: PAN-026552


	HRA iteration/version
	N/A


1.
Plan or Project Details
	Information about the plan or project  

	1
	Date application received

	Duly made 12/02/2025

	2
	Applicant details

	MSFT MCIO Limited

	3
	NRW team responsible for carrying out, or requiring to be carried out, the plan or project, and name of lead officer
	N/A

	4
	Activity/ies proposed


	The Applicant, MSFT MCIO Limited, has applied for a new bespoke permit that allows them to operate 31 emergency back-up generators at the proposed new Hyperscale Data Centre campus in Duffryn, Newport. The purpose of the generators is to supply electricity to the Data Centre in the event of a major power outage or black-out. The total rated thermal input of the generators is 236MW. The generators will operate via the combustion of diesel but have the capacity to be converted to run on hydrotreated vegetable oil (HVO) if required. 
The generators will be comprised of 28 emergency backup diesel generators, two administrative building generators and one water treatment plant generator. The permit relates to only this combustion activity, not the Data Centre operation itself. The generators will only ever operate during two scenarios: (i) for the purpose of routine testing and maintenance, and (ii) if a major power outage or black-out occurs that interrupts the electricity supply to the Data Centre. The generators are all fitted with selective catalytic reduction (SCR) abatement systems to facilitate the removal of oxides of nitrogen from the exhaust gases.
The routine testing and maintenance regime is as follows: 
· Monthly test – 15 minutes, 8 times per year (included in air dispersion modelling as 30% engine load);

· Quarterly test – 30 minutes, 3 times per year (included in air dispersion modelling as 70% engine load);

· Annual test – one hour, once per year (included in air dispersion modelling as 100% engine load);

· Annual PIT test – 90 minutes, once per year (included in air dispersion modelling as 60% engine load);

· Unit Substation (USS) Switchgear (Quinquennial) test – 90 minutes, once every five years (included in air dispersion modelling as 60% engine load); and

· Uninterruptable Power Supply (UPM) Switchgear (Quinquennial) test – 90 minutes, once every five years (included in air dispersion modelling as 60% engine load).
All generators will follow the same testing regime.

The emergency power outage scenarios are:

· 1 hour; and

· 72 hours.

Other than this, apart from very minimal additional testing should there be any faults unplanned maintenance (which will be short duration) the engines will remain off, and retained for emergency use only. 
Emergency use is considered to be very unlikely and there are extensive measures in place (in line with Best Available Techniques for the sector) to minimise the likelihood and duration of any national grid power failure (e.g. high voltage (HV) connection direct to “super grid” capable of powering the entire site, use of UPS (uninterruptable power supplies), etc.
Should emergency operation be required, generators would operate in emergency mode. The operator has modelled the impact of 1hr and 72hr emergency operation and has assumed that during these events, all engines would operate simultaneously and at 60% loading. If a permit is granted, these time and loading capacity restrictions will be included in the permit. 
Emergency operation would be a significant event for the site, and for the National Grid network, and would be immediately reported to NRW and managed as necessary as an incident. 
The generators will normally run on low sulphur conventional diesel, but Hydrotreated Vegetable Oil (HVO) may be used as a secondary backup fuel. 
They will be fitted with Selective Catalytic Reduction (SCR) for NOx emissions abatement. Each generator will operate for less than 500 hours per year and will be considered Limited Operating Hours Medium Combustion Plant (MCP) and exempt from the emission limit values within Schedule 25A of EPR. The emissions in the exhaust gases that area relevant to this HRA are: 
· Oxides of nitrogen (NOX as NO2)
· Particulate matter (PM)
· Sulphur Dioxide (SO2)
· Ammonia (NH3)



	5
	Relevant legislation or statutory basis

	Environmental Permitting (England and Wales) Regulations 2016 (EPR)
The Industrial Emissions Directive (IED)

The Medium Combustion Plant Directive (MCPD)

	6
	Location

	Imperial Park Business Park, Celtic Way, Duffryn, Newport, NP10 8BE

	7
	Plan or project documents, including any application documents
	See documents titled PAN-026552 dated 02/02/20254, 17/01/2025, 27/08/2025 and 08/10/2025
· In the DMS folder (internal)
· On the online Public Register (external)

	8
	Environmental Statement
	N/A

	9
	Pre-application correspondence 
	N/A

	10
	NRW team responsible for preparing this HRA report, and lead officer
	Victoria Seller
Lead Specialist Permitting Officer, Installations and RSR Permitting Team

	11
	Team or person responsible for approving the plan or project (competent authority role)
	Blaenau Gwent, Caerphilly & Newport Environment Team


2.
Determining the need for a Habitats Regulations Assessment

	2.1 Is there any possibility that the plan or project could negatively affect any European sites?
	Yes

	2.2 Is the whole of the plan or project directly and only connected with or necessary to the management of one or more European sites, for the purposes of conserving the habitats or species for which the European site(s) is/are designated?
	No

	2.3 Is there a possibility that the plan or project could affect any other feature of the European site(s) concerned, or of another European site, in a way that would undermine that feature’s conservation objectives?
	


3.
Considering the likelihood of a significant effect (LSE) 
3.1
Renewal of a project authorisation on the same or more restrictive terms as an extant authorisation
	Is this a renewal of an extant authorisation which complies with NRW approved criteria for ruling out significant effects of renewals (see Part 2 of OGN200) without conducting a project-specific LSE test?
	No


3.2
Likelihood of significant effects (LSE) test 
3.2.1 
Which European sites might be affected by the plan or project?
	(a)
	Based on the plan or project specification or information provided in the application, it is considered that these European sites have features which could be negatively affected by the plan or project
	[image: image2.png]: NG| M \ Transporter20p I
Gralg \'“ = // == \ LEIN4 Z > Br ol =

Saeson - K/ -~ OV 3
%‘\ g\d A Hopse;! /’
Courgtrv Parky





· Severn Estuary SAC / SPA / Ramsar
· River Usk (Lower Usk) / Afon Wysg (Wysg Isaf) SAC

	(b)
	The potential for the plan or project to negatively affect these European sites was also initially considered, but can be ruled out without further consideration
	Severn Estuary SAC/ SPA / Ramsar (England) – the boundary of the English designation is >10km from the facility, so it is considered that consultation with NRW protected sites advisors only (and not Natural England) is appropriate.


3.2.2 Screening for likelihood of significant effect
	TABLE 3.2.2  Screening assessment

	European site name: Severn Estuary SAC

	The notified features for this site (as detailed in the Severn Estuary Core Management Plan dated June 2009) are listed below:

1. Estuaries

2. Subtidal sandbanks

3. Intertidal mudflats and sandflats

4. Atlantic salt meadows

5. Reefs

6. River lamprey

7. Sea lamprey

8. Twaite shad
Estuaries is an over-arching feature which also includes all other listed features (which are also features in their own right).In addition, hard substrate habitats including eel grass beds, the estuary-wide assemblage of fish species and the assemblage of waterfowl species (for which the Ramsar Site and SPA are specifically designated – see below) are identified as notable estuarine assemblages which are an intrinsic part of the estuary ecosystem – these are therefore also covered by the “estuaries” feature. 
Conservation Objectives for the site are listed in the Core Management Plan linked above. 
The screening assessment below will consider the likelihood of significant effect from the changes to the permit proposed by the operator as detailed in section 1 of this form and any relevant conservation objectives.


	Potential impact pathway
	Screening conclusion – ‘SCREEN OUT’, ‘SCREEN IN’ or ‘IN COMB’

	Disturbance, Habitat Loss or Physical Damage 
Conservation objectives for the estuaries features (for which all other features are sub-features of) include objectives relating to its total extent and the physical form – see Core Management Plans for full list of objectives. 
The installation is located approximately 3.2km from the site and hence there is no likelihood of significant effects to any of the listed features from disturbance, habitat loss or physical damage which are typically associated with direct activity within a protected site boundary.
	SCREEN OUT - there is no potential impact from the plan or project on the sites features and a significant effect can be ruled out without further  assessment.

	Changes to the water column 

There are no emissions to water proposed as part of this permit variation. The only emissions to water will be uncontaminated surface water run-off. All potentially polluting hazardous substances (including fuel and AdBlue) will be suitably stored and contained to effectively minimise the risk of accidental release to water. Therefore there is no likelihood of significant effect to any of the listed features as a result of changes to the water column (flow regimes, thermal regimes, siltation etc).
	SCREEN OUT - there is no potential impact from the plan or project on the sites features and a significant effect can be ruled out without further assessment.

	Changes to air quality – Sulphur Dioxide (SO2) 

The engine emissions will contain minimal concentrations of sulphur due to the ultra-low sulphur content of the gas oil (diesel) fuel.
As noted above, the sites Estuaries feature is an over-arching feature for which other features are sub-features of. This estuarine & intertidal habitat is also a supporting habitat for the sites protected species. A relevant conservation objective for this feature is: 
“ix. Airborne nutrient and contaminant loads are below levels which would pose a risk to the ecological objectives described above” 

The Air Pollution Information System (APIS) website
 is used as the source of the environmental standards (“critical levels” and “critical loads”) for use in assessing the predicted impact of industrial pollutants on vegetation and ecosystems. The Core Management Plan explicitly specifies that concentrations of SO2 should not exceed the maximum critical load for the site. The applicant has considered the impact of SO2 emissions in their application. They have screened out SO2 emissions from requiring detailed assessment (modelling) on the basis that ultra-low sulphur diesel will be used (or HVO which is lower in sulphur again). They have instead used the modelled results for NOX and the sulphur content of the fuel to calculate / demonstrate low sulphur emissions (e.g. 0.110 µg/m3 for a single engine and 2.05 µg/m3 for all engines). We are in agreement of this approach in this instance when also considering the low operational hours of the engines (both planned and emergency operation). We do not anticipate there to be a likelihood of significant effect on the site from SO2 emissions as a result of the variation. This is the case for both the testing and emergency operation scenarios.
	SCREEN OUT - there is no potential impact from the plan or project on the sites features and a significant effect can be ruled out without further assessment.

	Changes to air quality – Ammonia (NH3) 
All engines will use SCR abatement (AdBlue) which may lead to emissions of Ammonia (NH3) should “ammonia slip” occur.

As discussed, a relevant conservation objective for the site’s Estuaries feature is:
“ix. Airborne nutrient and contaminant loads are below levels which would pose a risk to the 

ecological objectives described above”
The Core Management Plan explicitly specifies that concentrations of NH3 should not exceed the maximum critical level for the site, which is given as 3µ/m3 on APIS. The applicant has modelled potential emissions of ammonia against the lower NH3 critical level of 1µ/m3. We agree with the use of this critical level and consider the applicant’s approach to be conservative when compared to the Core Management Plan objective.

The applicant has also assessed emissions of NH3 based upon the anticipated total cumulative impacts of all tests undertaken as described above. We consider this to be an appropriate approach.

Changes to NH3 emissions as a result of the variation could impact the site via the following pathways: 

· Toxic contamination (from increased concentrations of airborne NH3)

The applicant has provided a detailed assessment of NH3 impacts, using detailed modelling to determine the significance of the NH3 emissions and deposition against the relevant environmental standards in line with relevant guidance. Impacts of testing and emergency usage have been assessed. 

Please refer to the air quality modelling report for a full description of modelling approach. We are in agreement with this approach. The assumptions underpinning the model have been checked and are reasonably precautionary. The way in which the applicant used dispersion models, its selection of input data, use of background data and the assumptions it made have been reviewed by Natural Resources Wales modelling specialists to establish the robustness of the applicant’s air impact assessment. These checks indicated that we are in general agreement with the modelling results and as such, they have been used to support this HRA assessment. 

The air quality modelled has calculated process contributions (PC) and predicted environmental concentrations (PEC) at locations within the Severn Estuary SAC and compared them against the relevant environmental standard to predict if impacts are to be significant using the accepted guidance on determining significance of air quality modelling results
. For screening of likely significant effects, impacts can generally be screened out where they are under 1% for long term impacts (please refer to guidance for further information). 

1. Testing 

1.1    Toxic contamination from airborne NH3 – long term assessment 

Emissions of NH3 were assessed against the long term critical level of 1 μg/m3. As discussed, NRW are in agreement with the critical level used. The maximum long term PC from the cumulative impact of all planned tests is 0.000194 μg/m3, which is less than 1% of the critical level. Therefore, in accordance with the relevant guidance, long term impacts can be considered insignificant. 

2. Emergency Operation – 1 hour 

2.1. Toxic contamination from NH3 – long term assessment 

Emissions of NH3 were assessed against the long term critical level of 1 μg/m3. As discussed, NRW are in agreement with the critical level used. The maximum long term PC 0.0000236 μg/m3 was predicted to be less than 1% of the critical level. Therefore, in accordance with the relevant guidance, long term impacts can be considered insignificant. 


3. Emergency operation – 72 hour 

3.1. Toxic contamination from NH3 – long term assessment 

Emissions of NH3 were assessed against the long term critical level of 1 μg/m3. As discussed, NRW are in agreement with the critical level used.  The maximum long term PC (0.0017 μg/m3 ) was predicted to be less than 1% of the critical level. Therefore, in accordance with the relevant guidance, long term impacts can be considered insignificant. 
	SCREEN OUT - there is no potential impact from the plan or project on the sites features and a significant effect can be ruled out without further assessment.

	Changes to air quality – Oxides of Nitrogen (NOX) (mixture of NO and NO2) 

The engine emissions will contain oxides of NOX which is a principle pollutant of concern for this activity. As discussed, a relevant conservation objective for the site’s Estuaries feature is: 
“ix. Airborne nutrient and contaminant loads are below levels which would pose a risk to the ecological objectives described above” 
The Core Management Plan explicitly specifies that concentrations of NOX should not exceed the maximum critical load for the site. Changes to NOX emissions as a result of the variation could impact the site via the following pathways: 
· Toxic contamination (from increased concentrations of airborne NOX)
· Nutrient enrichment (from NOX deposition)
· Acidification (acid deposition from Nitrogen (N) and Sulphur (S)) 
The applicant has provided a detailed assessment of NOX impacts, using detailed modelling to determine the significance of the NOX emissions and deposition against the relevant environmental standards in line with relevant guidance
. Impacts of testing and emergency usage have been assessed. 
Please refer to the air quality modelling report for a full description of modelling approach. We are in agreement with this approach. The assumptions underpinning the model have been checked and are reasonably precautionary. The way in which the applicant used dispersion models, its selection of input data, use of background data and the assumptions it made have been reviewed by Natural Resources Wales modelling specialists to establish the robustness of the applicant’s air impact assessment. These checks indicated that we are in general agreement with the modelling results and as such, they have been used to support this HRA assessment. 
The air quality modelled has calculated process contributions (PC) and predicted environmental concentrations (PEC) at locations within the Severn Estuary SAC and compared them against the relevant environmental standard to predict if impacts are to be significant using the accepted guidance on determining significance of air quality modelling results. For screening of likely significant effects, impacts can generally be screened out where they are under 10% for short term impacts and 1% for long term impacts (please refer to guidance for further information). 
1. Testing 
1.1. Toxic contamination from airborne NOX – short term assessment 
Potential impact of short-term (daily) NOX emissions on the Severn Estuary SAC has been based upon the anticipated worst-case scenario of the quinquennial test, as it represents worst-case impact in any 24-hour period during routine testing. As for NH3, the applicant has based their assessment of short-term (daily) NOX upon the anticipated total cumulative impacts of all tests undertaken as described above. We consider this methodology to appropriate.

Emissions of NOX have been assessed against a short term (daily) critical level of 200 micrograms per cubic metre (μg/m3). Whilst the standard critical level for NOX for protected sites is usually 75 μg/m3, 200 μg/m3 has been used where ozone is below the AOT critical level and sulphur dioxide is below the critical level of 10 μg/m3. This approach is line with guidance
 and NRW are in agreement with the critical level used. 
The maximum short-term Process Contribution (PC) (2.24 μg/m3) was predicted to be less than 10% of the critical level. Therefore, in accordance with the relevant guidance, short-term impacts can be considered insignificant. 
1.2 Toxic contamination from airborne NOX – long term assessment 
Long-term assessment (annual) of testing impacts included an accumulation of the impact from all planned testing regimes. Emissions of NOX were assessed against the long term critical level of 30 μg/m3. As discussed, NRW are in agreement with the critical level used. The maximum long-term PC (0.00529 μg/m3) was predicted to be less than 1% of the critical level. Therefore, in accordance with the relevant guidance, long-term impacts can be considered insignificant. 
1.3 Nutrient enrichment from NOX deposition 
NOX deposition has been assessed against a minimum critical load of 10 kgN/ha/yr. APIS lists a critical load range of 10-20 N kg/ha/yr for the site’s most sensitive feature (estuaries). For assessment, it is recommended the minimum value of the critical load range is used, which in this case would be 10 kgN/ha/hr. We therefore consider the applicant’s use of 10 kgN/ha/yr to be appropriate.

The applicant’s assessment reported that maximum PC (0.00258 kgN/ha/yr) was predicted to be less than 1% of a critical load of 10 kgN/ha/yr. Therefore, in accordance with the relevant guidance impacts can be considered insignificant. 
1.4 Acidification from acid deposition 
At the time of this assessment, there were no acidity critical loads listed on APIS for the Severn Estuary SAC. In most cases where there are no critical loads listed for acidity, acidity impacts can be screened out on the basis of an assumption of no sensitivity or lack of known sensitivity. Consequently, the applicant has not modelled the impact of airborne deposition of acid gases on the SAC.
There are no Conservation Objectives in the Severn Estuary SAC Core Management Plan that relate specifically to acid deposition from airborne sources. APIS indicates that three of the Annex II species listed in the Core Management Plan are sensitive to acidification of freshwater habitat; however, there is no pathway mechanism to enable the deposition of airborne acid gases into water. Therefore, for this reason, and those outlined above, we consider that the impact from acid deposition can be considered insignificant, in accordance with relevant guidance.
2. Emergency Operation – 1 hour 
2.1. Toxic contamination from NOX – short term assessment 
Emissions of NOX were assessed against a short term critical level of 200 μg/m3. As discussed, this approach is line with guidance and NRW are in agreement with the critical level used.

The maximum short term PC (1.5 μg/m3) was predicted to be less than 10% of the short term critical level. Therefore, in accordance with the relevant guidance, short-term impacts can be considered insignificant. 
2.2. Toxic contamination from NOX – long term assessment 
Emissions of NOX were assessed against the long term critical level of 30 μg/m3. As discussed, NRW are in agreement with the critical level used. The maximum long term PC (0.000506 μg/m3) was predicted to be less than 1% of the critical level. Therefore, in accordance with the relevant guidance, long-term impacts can be considered insignificant. 


2.3. Nutrient enrichment from NOX deposition 
NOX deposition has been assessed against a minimum critical load of 10 kgN/ha/yr. APIS lists a critical load range of 10-20 N kg/ha/yr for the site’s most sensitive feature (estuaries). For assessment, it is recommended the minimum value of the critical load range is used, which in this case would be 10 kgN/ha/hr. We therefore consider the applicant’s use of 10 kgN/ha/yr to be appropriate.

The applicant’s assessment reported that maximum PC (0.00286 kgN/ha/yr) was predicted to be less than 1% of a critical load of 10 kgN/ha/yr. Therefore, in accordance with the relevant guidance impacts can be considered insignificant. 
2.4. Acidification from acid deposition 
At the time of this assessment, there were no acidity critical loads listed on APIS for the Severn Estuary SAC. In most cases where there are no critical loads listed for acidity, acidity impacts can be screened out on the basis of an assumption of no sensitivity or lack of known sensitivity. Consequently, the applicant has not modelled the impact of airborne deposition of acid gases on the SAC.

There are no Conservation Objectives in the Severn Estuary SAC Core Management Plan that relate specifically to acid deposition from airborne sources. APIS indicates that three of the Annex II species listed in the Core Management Plan are sensitive to acidification of freshwater habitat; however, there is no pathway mechanism to enable the deposition of airborne acid gases into water. Therefore, for this reason, and those outlined above, we consider that the impact from acid deposition can be considered insignificant, in accordance with relevant guidance.

3. Emergency operation – 72 hour 
3.1. Toxic contamination from NOX – short term assessment 
Emissions of NOX were assessed against a short term critical level of 200 μg/m3. As discussed, this approach is line with guidance1 and NRW are in agreement with the critical level used. 
The maximum short term PC (35.9 μg/m3) was predicted to be more than 10% (17.95%). Therefore, in accordance with the relevant guidance, impacts cannot be screened out as insignificant and appropriate assessment is required. 
Emissions of NOX were assessed against a short term critical level of 200 μg/m3. The maximum short term PEC was calculated to be 88.1 μg/m3. This is 44% of the critical level which indicates there is a risk of the critical level being significantly exceeded during a 72 hour emergency outage.
3.2. Toxic contamination from NOX – long term assessment 
Emissions of NOX were assessed against the long term critical level of 30 μg/m3. As discussed, NRW are in agreement with the critical level used. 
The maximum long term PC (0.0364 μg/m3) was predicted to be less than 1% of the critical level. Therefore, in accordance with the relevant guidance, long term impacts of air pollution from NOX can be considered insignificant. 
3.3. Nutrient enrichment from NOX deposition 
NOX deposition has been assessed against a minimum critical load of 10 kgN/ha/yr. APIS lists a critical load range of 10-20 N kg/ha/yr for the site’s most sensitive feature (estuaries). For assessment, it is recommended the minimum value of the critical load range is used, which in this case would be 10 kgN/ha/hr. We therefore consider the applicant’s use of 10 kgN/ha/yr to be appropriate.

The applicant’s assessment reported that maximum PC (0.0206 kgN/ha/yr) was predicted to be more than 1% (2.92%) of a critical load of 10 kgN/ha/yr. Therefore, in accordance with the relevant guidance impacts can be considered insignificant. 
3.4. Acidification from acid deposition 
At the time of this assessment, there were no acidity critical loads listed on APIS for the Severn Estuary SAC. In most cases where there are no critical loads listed for acidity, acidity impacts can be screened out on the basis of an assumption of no sensitivity or lack of known sensitivity. Consequently, the applicant has not modelled the impact of airborne deposition of acid gases on the SAC.

There are no Conservation Objectives in the Severn Estuary SAC Core Management Plan that relate specifically to acid deposition from airborne sources. APIS indicates that three of the Annex II species listed in the Core Management Plan are sensitive to acidification of freshwater habitat; however, there is no pathway mechanism to enable the deposition of airborne acid gases into water. Therefore, for this reason, and those outlined above, we consider that the impact from acid deposition can be considered insignificant, in accordance with relevant guidance.


	Testing 
‘IN COMB’ - a significant effect on the feature when considered alone can be ruled out without further assessment, but the potential for a significant effect on the feature from this plan or project in combination with the effects of other plans or projects, needs to be considered. 

Emergency operation – 1 hr 
‘IN COMB’ - a significant effect on the feature when considered alone can be ruled out without further assessment, but the potential for a significant effect on the feature from this plan or project in combination with the effects of other plans or projects, needs to be considered. 

Emergency operation – 72 hr 
SCREEN IN - there is a potential impact from the plan or project on the sites features and a significant effect cannot be ruled out without further assessment 

	Smothering 
The engines will emit particulate matter. While particulate matter does not have a Critical Level or Load set for the protection of vegetation and ecosystems, it still has the potential to contribute to smothering of vegetation from airborne fallout. PM10 & PM2.5 Particulate Matter are deposited slowly but may travel 1000m or more. However, concentrations decrease rapidly on moving away from the source, due to dispersion and dilution. At the closest point of the SAC is located 3.2km from the site, we consider that in this case there is no realistic likelihood of impact.
	SCREEN OUT - there is no potential impact from the plan or project on the sites features and a significant effect can be ruled out without further assessment.

	European site name: Severn Estuary SPA and Severn Estuary Ramsar

	Likelihood of significant effect will be assessed for both these sites together as the site boundaries are the same. 
The notified features for the Severn Estuary SPA site (as detailed in The Severn Estuary Core Management Plan dated June 2009) are listed 

below:

1. Berwick swan

2. European white-fronted goose

3. Dunlin

4. Redshank

5. Shelduck

6. Gadwall

7. Internationally important assemblage of waterfowl
The notified features for the Severn Estuary Ramsar site (also detailed in the Severn Estuary Core Management Plan dated June 2009) are: 

1. Estuaries 

2. Assemblage of migratory fish species (includes Sea Lamprey, River Lamprey, Twaite Shad, Allis Shad, Salmon, Sea Trout and Eel)

3. Bewick Swan

4. European white-fronted goose

5. Dunlin

6. Redshank

7. Shelduck

8. Gadwall 

9. Internationally important assemblage of waterfowl. 
For all these listed species, the estuaries feature and it’s sub-features (notably intertidal mudflats and sandflats, Atlantic salt meadows and 

hard substrate habitats ) provides an important supporting habitat. 
Conservation Objectives for the site are listed in the Core Management Plan linked above. 
The screening assessment below will consider the likelihood of significant effect from the changes to the permit proposed by the operator as 

detailed in section 1 of this form and any relevant conservation objectives.



	Potential impact pathway
	Screening conclusion – ‘SCREEN OUT’, ‘SCREEN IN’ or ‘IN COMB’

	Disturbance, Habitat Loss or Physical Damage 
See comments for Severn Estuary SAC above.

	SCREEN OUT – there is no potential impact from the plan or project on the site features and a significant effect can be ruled out without further assessment.

	Changes to the water column 

See comments for Severn Estuary SAC above.
	SCREEN OUT – there is no potential impact from the plan or project on the site features and a significant effect can be ruled out without further assessment.

	Changes to air quality – Sulphur Dioxide (SO2) 

See comments for Severn Estuary SAC above.
	SCREEN OUT – there is no potential impact from the plan or project on the site features and a significant effect can be ruled out without further assessment.

	Changes to air quality – Ammonia (NH3) 

See comments for Severn Estuary SAC above.
	SCREEN OUT – there is no potential impact from the plan or project on the site features and a significant effect can be ruled out without further assessment.

	Changes to air quality - Oxides of Nitrogen (NOX) (mixture of NO and NO2)
See comments for Severn Estuary SAC above.
	Testing 
‘IN COMB’ - a significant effect on the feature when considered alone can be ruled out without further assessment, but the potential for a significant effect on the feature from this plan or project in combination with the effects of other plans or projects, needs to be considered. 

Emergency operation – 1 hr 
‘IN COMB’ - a significant effect on the feature when considered alone can be ruled out without further assessment, but the potential for a significant effect on the feature from this plan or project in combination with the effects of other plans or projects, needs to be considered. 

Emergency operation – 72 hr 
SCREEN IN - there is a potential impact from the plan or project on the sites features and a significant effect cannot be ruled out without further assessment

	Smothering 

See comments for Severn Estuary SAC above.
	SCREEN OUT – there is no potential impact from the plan or project on the site features and a significant effect can be ruled out without further assessment.

	European site name: River Usk SAC

	The notified features for the River Usk SAC site (as detailed in River Usk SAC Core Management Plan dated 2022) are listed below:

• Sea lamprey 

• Brook lamprey 

• River lamprey 

• Twait shad 

• Allis shad 

• Atlantic Salmon 

• Bullhead 

• European otter 

• Watercourses of plain to montane levels 
Conservation Objectives for the site are listed in the Core Management Plan linked above.
The screening assessment below will consider the likelihood of significant effect from the changes to the permit proposed by the operator as 

detailed in section 1 of this form and any relevant conservation objectives.



	Potential impact pathway
	Screening conclusion – ‘SCREEN OUT’, 

‘SCREEN IN’ or ‘IN COMB’

	Disturbance, Habitat Loss or Physical Damage 
The installation is located approximately 3 km from the site and therefor comments made 

for Severn Estuary SAC apply here also.
	SCREEN OUT - there is no potential impact from the plan or project on the sites features and a significant effect can be ruled out without further assessment.

	Changes to the water column

See comment for the Severn Estuary SAC above.
	SCREEN OUT - there is no potential impact from the plan or project on the sites features and a significant effect can be ruled out without further assessment.

	Changes to air quality

As discussed, there is a risk of impact to features from changes to NOx, SO2 and NH3 emissions as a result of the variation. However, the in-river/riverine features (i.e. all apart from European otter) listed are not considered sensitive to airborne NO2, acidic gases such as SO2 and NH3 and environmental standards for further assessment are not considered applicable. As such, further consideration of the impacts from toxic contamination, nutrient enrichment or acidification is not required. Otters and their prey are also not sensitive to aerial sources of NOx, acidic gases such as SO2 and NH3. It is not considered there will be emissions at rates high enough to cause any damage to vegetation used by the otters for resting and breeding sites due to the nature of the proposed engine use (testing and emergency operations). Therefore, we consider that there is unlikely to be any reduction in the features quality or extent of otter habitat associated with this variation as a result of nutrient enrichment or acidification and further consideration of these impacts are not required.
	SCREEN OUT - there is no potential impact from the plan or project on the sites features and a significant effect can be ruled out without further assessment.

	Smothering
See comments for Severn Estuary SAC above.
	SCREEN OUT - there is no potential impact from the plan or project on the sites features and a significant effect can be ruled out without further assessment.


	TABLE 3.2.3 Screening decision of the plan or project ‘alone’



	(a) If the screening conclusion for all features for all sites in Table 3.2.2 is ‘SCREEN OUT’
	The plan or project is not likely to have a significant effect on any European site, and no further consideration under the Habitats Regulations is required in order to determine the approval/application.


	(b) If the conclusion for any features in Table 3.2.2 is ‘SCREEN IN’ 
	The plan or project is likely to have a significant effect on one or more European sites and therefore an appropriate assessment is required.


	(c) If there are no features in Table 3.2.2 that are ‘SCREEN IN’ and any features that are ‘IN COMB’
	The plan or project is not likely to have a significant effect on any European sites when considered alone, but the possibility of significant effects in combination with other plans and projects needs to be considered.



4.
Appropriate assessment of the plan or project when considered alone
4.1
Assessment of plan or project as defined
	Table 4.1 Appropriate assessment of the plan or project as defined 


	European site name: Severn Estuary SAC / SPA / Ramsar
	Can adverse effects on site integrity be ruled out? ‘YES’ or ‘NO’

	As identified in section 3, the site’s estuaries feature and its sub-features (and hence the species it supports) are potentially sensitive to NOX emissions and a conservation objective is to keep concentrations of this pollutant below the set critical levels and loads. The Core Management Plan is clear in that the estuaries feature and it’s sub features are supporting habitats to the species which are features of the SPA and RAMSAR
This appropriate assessment will focus on the potential impacts from NOX emissions from the emergency operation (that did not screen out as insignificant) of the engine arrangement when used as a backup energy supply. For detailed modelling there is no criteria to decide whether PCs are significant. To judge significance, the applicant has considered background concentrations of NOX. Predicted Environmental Contribution (PEC), which is the predicted PC and the existing background concentrations, has been calculated as percentage of the relevant critical level or load to determine if there is a risk of standard being breached. Results discussed represent maximum point of impact within the site’s boundary.

	YES

	Emergency Operation – 72 hours 

1. Toxic contamination from airborne NOX – short term assessment 

Emissions of NOX were assessed against a short term critical level of 200 μg/m3. The maximum short term PEC was calculated to be 88.1 μg/m3. This is 44% of the critical level which indicates there is a risk of the critical level being significantly exceeded during a 72 hour emergency outage. This is based on the most recent guidance for data centres and is considered extremely conservative. We do not normally assess the impact of unexpected emergency emissions and an appropriate approach is needed for back-up engines. 
Detailed modelling which considers every year of operation for 5 years of meteorological data, has found that the above is the absolute maximum impact on the Severn Estuary SAC could be above the short term critical level, as a daily average based on the engines running for 72 hours. However, for this impact to occur, worst case weather (dispersion) characteristics would have to occur for the full 72 hours at the same time as a very rare power supply interruption. 
Emergency operation of all of the engines to provide back-up power is a very rare event. If the permit is granted, the data centre will be designed with high availability (99.999% uptime) with a distributed redundancy design philosophy, meaning that the data centre will be resilient to equipment failures with each power string having two uninterruptible power supplies (UPS) in addition to generators. Equipment will be designed to be concurrently maintainable, allowing maintenance without running on generators. In addition, the data centre will be protected from short term brown-outs or black-outs by the UPSs. These buffer small fluctuations in electrical supply.
There are no standard permitting criteria for assessing risk from possible, but unlikely, emergency events. Given that a long term air emission level is regarded as insignificant if it is less than 1% of the critical level, it is considered that a less than 1% likelihood of exceedance in an emergency is similarly an insignificant risk to the protected site. In a permit is granted, conditions within that permit conditions would limit the number of hours of emergency operation. Permit conditions would be reviewed if the likelihood of emergency operation substantially changed. 
If granted, the permit will include additional controls to protect the environment in the event of emergency operation. These include an Air Quality Management Plan (AQMP) which requires the operator to notify NRW in the event of any emergency operation. The limits of the permitted activity will specifically state that emergency generation shall cease or be reduced if there is credible information that there may an immediate significant adverse effect on the environment (detailed in the permit’s Table S1.1). 
For the reasons discussed above, it is therefore considered that based on this information in the application, there is no risk of adverse impact on the site integrity. 

	


4.2
Appropriate assessment of the plan or project taking into account additional conditions or restrictions imposed by the competent authority
	Table 4.2 Appropriate assessment of the plan or project taking into account additional conditions or restrictions

	European site Feature 
	Adverse effect(s)
	Can adverse effect(s) be mitigated by additional imposed conditions or restrictions?
‘YES’ or ‘NO’
	Additional imposed mitigation measure(s) 


	Can adverse effect on site integrity be ruled out?
‘YES’ or ‘NO’

	European site name: Severn Estuary SAC / SPA / Ramsar

	N/A – There is no requirement to consider additional measures as it has been shown that impact alone can be ruled out as having adverse effect on site integrity. This is partly due to nature of the operation and mitigation measures in the form of SCR which are integral to the proposal as put forward by the applicant. The Operator will be required to operate as per the application proposal through the permits operating techniques.


4.3 
Concluding the appropriate assessment of the plan or project alone

	Table 4.3 Conclusion of the appropriate assessment alone

	(a) If Table 4.1, or the right hand column of Table 4.2 if applicable, is ‘YES’ for all features 
	It has been ascertained that the plan or project, when considered alone, will not adversely affect the integrity of any European sites. 



	(b) If there are any ‘NO’s in the right hand column of Table 4.2
	It has not been ascertained that the plan or project, when considered alone, will not adversely affect the integrity of one or more European sites. 


	(c) Are there any residual effects of the plan or project (net of mitigation measures) which, though not adverse on their own, could be significant when considered in combination with the effects of other plans or projects?
	YES


5.
In combination assessment

	Table 5.1 Identification and assessment of in combination effects

	European site name: Severn Estuary SAC / SPA / Ramsar


	For the purpose of the in-combination assessment, impacts at the 3 Severn Estuary sites will be discussed together.
Potential in combination effects to be considered:

It has been ascertained, following assessment of the applicant’s air quality modelling, that the impact of changing emissions from the 

proposed Hyperscale Data Centre will have no adverse impact on the sites’ integrity. Whilst impact has been determined to not adversely impact 

the site alone, there are residual impacts which could act in combination with other relevant plans/projects in the area. This assessment will

consider these, and the impact pathways screened out as insignificant alone in section 3 (LSE) but identified as having potential residual 

effects in-combination (i.e. checking if effects of the projects in combination won’t make insignificant effect significant).

As discussed in this assessment, the Severn Estuary SAC / SPA / Ramsar estuaries feature (and its sub-features), are sensitive to air 

pollution impacts. These include toxic contamination from ambient NOX and nutrient enrichment from NOx deposition.
Relevant projects which have been considered for the inclusion in an in-combination assessment include: 

· Recent (March 2025) variation (ref. PAN-026558) to and original application (ref. PAN-019560) for an environmental permit for to the Newport Data Centre (CWL 11 and 12) permit operated by Vantage Data Centers UK Ltd. (permit number EPR/BB3599CW), located 575 m to the north-east; and
· Recent (November 2024) variation (ref. PAN-024049) to the Newport Semi Conductor Facility permit operated by IQE Silicon Compounds Ltd. (permit number EPR/AB2893FZ), located 570m to the east.
These have the potential to be relevant projects as they are associated with emissions of NOX which would not have been captured in background concentration data. 

For the Data Centres, the applicant has considered only the cumulative impacts from testing activities, and omitted assessment of the emergency scenarios due to the rare occurrence of prolonged power outages. The combined operations of the MSFT site and Newport Data Centre (CWL 11 and 12) undertaking testing operations has been evaluated based upon the anticipated total cumulative impacts of all tests undertaken, assuming coincident operation for a conservative basis. We agree with this approach.

The applicant’s in combination assessment also includes the impact associated with a proposal for a new Energy from Waste (co-incinerator) installation at Newport Docks, which is located approximately 3.8 km to the east of the proposed Hyperscale Data Centre. An application from Vital Energi Ltd. for a new environmental permit for this proposed installation has been submitted to NRW for determination. However, during the determination of the MSFT environmental permit application, the Installations and RSR Permitting Team has been contacted by Vital Energi Ltd. to withdraw their permit application. 

The applicant’s in combination assessment therefore presents a conservative assessment of cumulative impact, as, given the continuous operation, and large mass volume of emissions associated with the proposed co-incinerator, the assessment presented in the applicant’s report represents a significant overestimation of the impact from airborne NOx on the Severn Estuary.

[image: image3.png]L

3 AN i \'
.~ bcww. | ENC/NRW | Contains OS data © Crown Copyright and database right 202




Table 1: in combination PCs as percentages of the relevant AQS including and excluded contributions from the proposed co-incinerator

 

Process Contributions (PC)

Sum PCs (all)

Sum PCs (exc. ERF)

AQS (µg/m3 or kgN/ha/yr)

Sum of PCs (inc. ERF) as a %age of the AQS

Significant?

Sum of PCs (exc. ERF) as a %age of the AQS

Significant?

 

VDC

MSFT

IQE

ERF

Annual mean NOx
0.0314

0.003872

0

1.2

1.23527

0.035272

30

4.117573333

>1%

0.117573333

<1%

Daily mean NOx
0.981

2.24

0.06

9.6

12.881

3.281

200

6.4405

<10%

1.6405

<10%

Nutrient nitrogen deposition

0.0017

0.0795

0

0.27

0.3512

0.0812

10

3.512

>1%

0.270666667

<1%

Key

VDC

Newport Data Centre (CWL 11 and 12)

MSFT 

Hyperscale Data Centre

IQE

Newport Semi Conductor Facility

ERF

Co-incinerator

AQS

Air Quality Standard

Table 1 shows the summed PCs for annual mean NOx, daily mean NOx and nutrient nitrogen deposition for the four facilities as percentages of the relevant air quality standards. Removing the contribution from the co-incinerator (ERF), the summed PCs are all less that the relevant significance thresholds. The applicant’s assessment has therefore shown that for all tests, in combination impacts (under the worse meteorological conditions from a 5-year period assessed) screen out as being insignificant at the Severn Estuary SAC, SPA and Ramsar. 
For these reasons it is considered that there is no risk of adverse impacts on the sites’ integrity as result of the impacts in-combination of Hyperscale Data Centre, Newport Data Centre (CWL 11 and 12) and Newport Semi Conductor Facility.


	Can significant or adverse in combination effects be ruled out for all features? YES



	Table 5.2 In combination assessment: results

	(a) If the answer for all features considered in Table 5.1 is ‘YES’
	The plan or project, when considered in combination with other plans and projects, is either not likely to have a significant effect on, or will not adversely affect the integrity of, any European site. 



	(b) If the answer for any features considered in Table 5.1 is ‘NO’
	The plan or project in its current form is likely to have a significant effect on, or an adverse effect on, European site/s in combination with other plans or projects.  



6.
Conclusion
	HRA is not required because there is no conceivable impact on any European sites.

(As documented in section 2.1)
	

	HRA is not required because the whole of the plan or project is directly connected with or necessary to the management of one or more European sites, for the purposes of conserving the habitats or species for which the site(s) is/are designated, and the plan or project is not likely to have a significant effect on any other European sites.

(As documented in section 2.2 and 2.3)
	

	This project is a renewal of a current permission which complies with NRW agreed criteria for ruling out likely significant effects of a renewal without conducting a project-specific LSE test. Therefore, it is considered not likely to have a significant effect on any European sites, either alone or in-combination with other plans or projects.

(As documented in section 3.1 of this form)
	

	The plan or project has been screened for likelihood of significant effects and is considered not likely to have a significant effect on any European sites. (As documented in section 3.2 of this form, and section 5 if applicable) 
	

	In light of the conclusions of an appropriate assessment it has been established that the plan or project will not adversely affect the integrity of any European sites, taking into account any conditions or restrictions as applicable, either alone or in-combination with other plans or projects.
(As documented in section 4 of this form, and section 5 if applicable)
	X

	In light of the conclusions of the appropriate assessment, it has not been ascertained that the plan or project will not adversely affect the integrity of any European sites, as documented in section 4 of this form, and section 5 if applicable.
Approval for the plan or project cannot be given unless either:

· the plan or project specification, and/or the terms under which it might be approved, are modified so as to remove the risk of adverse effects, and a revised HRA is prepared, or

· the plan or project (not being an SSSI consent*) satisfies the requirements for a derogation and a Derogation Notice is prepared and submitted for consideration by the appropriate authority, normally Welsh Ministers
(*SSSI consents cannot be given as derogations)
	

	Signed: Victoria Seller
Name: Victoria Seller                                                               Position: Lead Specialist Permitting Officer 
Date: 23/10/2025


	Was this HRA conclusion an escalated decision? YES or NO
	 NO


7.
Consultation with the ANCB and how sections 2, 3, 4 and 5 of this HRA report (as applicable) take into account that advice.

	Relevant section of the HRA report
	Correspondence and/or meetings with the ANCB

	Description of how the comments from the ANCB have been taken into account

	2

	
	

	3
	
	

	4
	
	

	5
	
	


8.
Countersignature
	I have reviewed the HRA documented in this form and confirm that I agree/do not agree with the conclusion recorded in section 6.

Additional comments (if any):

Signed:

Name:
Position:

Date:




� �HYPERLINK "https://www.apis.ac.uk/"��Air Pollution Information System | Air Pollution Information System�


� �HYPERLINK "https://www.gov.uk/guidance/environmental-permitting-air-dispersion-modelling-reports"��Environmental permitting: air dispersion modelling reports - GOV.UK�


� �HYPERLINK "https://www.gov.uk/guidance/air-emissions-risk-assessment-for-your-environmental-permit"��Air emissions risk assessment for your environmental permit - GOV.UK�


� �HYPERLINK "https://www.gov.uk/guidance/environmental-permitting-air-dispersion-modelling-reports"��Environmental permitting: air dispersion modelling reports - GOV.UK�





www.naturalresources.wales








Page 20 of 20

