Sump Inventory and Inspection Summary

	Tank No.
	Name
	Location
	Material Stored
	Volume
	Above or

Below Ground
	Secondary Containment
	Testing
	Characteristics
	Inspection Date
	Comments

	S1
	Final Effluent Sump
	Yard
	Process Effluent
	100 lts
	Below
	None
	12 monthly Visual Inspection, in-house

12 monthly sump emptied by contractor to allow for visual inspection 
	Flows into foul sewer S1

Material:

Reinforced 
	16.12.25
	No failure of sump integrity observed

Residues of toy grade pigments on side

	S2
	Outer Sump
	Yard
	Process Effluent
	3000 lts
	Below
	None
	12 monthly Visual Inspection, in-house

12 monthly sump emptied by contractor to allow for visual inspection 
	Weir located at about 1.5 meter from bottom of sump. Effluent flowing across weir into final effluent sump S1

Material:
Reinforced concrete, PE lined
	16.12.25
	No failure of sump integrity observed

No damage to lining.


	S3
	Middle Sump
	Cellulose dept, RTTM
	Process Effluent
	5000 lts
	Below
	None
	12 monthly Visual Inspection, in-house

12 monthly sump emptied by contractor to allow for visual inspection 
	Effluent automatically pumped from sump S3 to outer sump S2 (float switch)

Material:

Reinforced concrete
	16.12.25
	No failure of sump integrity observed

Residues of toy grade pigments on side

Solids trap has been emptied of cellulose tubing

Cover has been added over middle sump

	S4
	Preservative Preparation Sump
	Cellulose dept, Preservative Preparation Area
	Process Effluent
	1000 lts
	Below
	None
	12 monthly Visual Inspection, in-house

12 monthly sump emptied by contractor to allow for visual inspection 
	Effluent from sump S5 is flowing into sump S4

Material:

Reinforced concrete
	16.12.25
	No failure of sump integrity observed

	S5
	Cellulose Print Sump


	Cellulose dept, Cellulose Printer
	Process Effluent
	1000 lts
	Below
	None
	12 monthly Visual Inspection, in-house

12 monthly sump emptied by contractor to allow for visual inspection 
	Effluent flowing under gravity from sump S5 into sump S4

Material:

Reinforced concrete
	16.12.25
	No failure of sump integrity observed


S3


[image: image1.emf]
S4


[image: image2.emf]
S2


[image: image3.emf]
S1


[image: image4.emf]
Review date

Who


Comment

16.12.25


R. Williams

Date:16.12.25
                                                                                    Page 9 of 9
Review date:





