Permit Number: 
BV9713IU


Operator: 

BOC Limited

Installation:

Margam Gases

Form Number: 
Performance1 / 25/04/07
Reporting of other performance indicators for the period 1 Jan 2025 to 31 Dec 2025
	Parameter
	
	Units 
	

	
	
	
	

	Total raw material used 
	633.97 Tonnes
	

	Total mass emissions to air:

Carbon monoxide

Oxides of Nitrogen
	242 kg

2585 kg
	

	Annual production:

Hydrogen
	175.29 Tonnes
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


	Operator’s comments:

Raw Material is Natural Gas



Signed: David Millerchip, Snr SHEQ Advisor









Date: 26/01/2026
Permit Number: 
BV9713IU


Operator: 

BOC Limited

Installation:

Margam Gases

Form Number: 
 Air1 / 25/04/07
Reporting of emissions to air for the period from 1 Jan 2025 to 31 Dec 2025 

	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Reference Period
	Result [1]
	Test

Method [2]
	Sample

Date and Times [3]
	Uncertainty

[4]

	A1
	Oxides of Nitrogen
	250 mg/m3
	Periodic over a minimum of a 4 hour period.  Data reported as half hourly averages.
	Shut down since 01/01/11
	ISO 10849: 1996
	
	

	A1
	Carbon Monoxide
	20 mg/m3
	Periodic with a minimum sampling time of 1 hour
	Shut down since 01/01/11
	BS EN15058
	
	

	A2
	Oxides of Nitrogen
	250 mg/m3
	Periodic over a minimum of a 4 hour period.  Data reported as half hourly averages.
	248 mg/m3
	SRM - BS EN 14792:2017
	21 October 2025
12h30 – 16h30
	+/- 12

	A2
	Carbon Monoxide
	50 mg/m3
	Periodic with a minimum sampling time of 1 hour
	23 mg/m3
	SRM - BS EN 15058:2017
	21 October 2025
12h30 – 16h30
	+/- 4.8


The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. gas chromatography.

For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   

The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

Signed: David Millerchip, Snr SHEQ Advisor.








Date: 26/01/2026
Permit Number: 
BV9713IU


Operator: 

BOC Limited

Installation:

Margam Gases

Form Number: 
Energy1 / 25/04/07
Reporting of Energy Usage for the year: 2025
	Energy Source
	Energy Usage
	Specific Usage

(MW/unit output)
	

	
	Quantity
	Primary Energy

(MWh)
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	Electricity *
	926 MWh
	2222 MWh
	12.6 MWh/Te
	

	Natural Gas
	4788 MWh
	4788 MWh
	27.3 MWh/Te
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	TOTAL
	5714 MWh
	7010 MWh
	39.9 MWh/Te
	

	
	
	
	
	


* Conversion factor for delivered electricity to primary energy = 2.4
	Operator’s comments: 
Specific Usage based on primary energy values.
Conversion factor for delivered electricity to primary energy provided by NRW 2024.



Signed: David Millerchip, Snr SHEQ Advisor  








Date: 26/01/2026
Permit Number: 
BV9713IU


Operator: 

BOC Limited

Installation:

Margam Gases

Form Number: 
Sewer1 / 25/04/07
Reporting of emissions to sewer for the period from 1 Jan 2025 to 31 Dec 2025 ……………………

	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Reference Period
	Result [1]
	Test

Method [2]
	Sample

Date and Times [3]
	Uncertainty

[4]

	S1
	pH
	pH 6-10
	Spot
	8.9
	SCA Blue Book Number 14, ISBN 0117514284
	71 different samples taken throughout the year.
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	


[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. gas chromatography.

[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   

[4] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.
Signed: David Millerchip, Snr SHEQ Advisor









Date: 22/01/26
Permit Number: 
BV9713IU


Operator: 

BOC Limited

Installation:

Margam Gases

Form Number: 
WaterUsage1 / 25/04/07
Reporting of Water Usage for the year 2025
	Water Source
	Usage

(m3/year
	Specific Usage 

(m3/unit output)
	

	
	
	
	

	
	
	
	

	Mains water
	2360
	13.46m3/Te H2
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	TOTAL WATER USAGE
	2360
	13.46m3/Te H2
	


	Operator’s comments:




Signed: David Millerchip, Snr SHEQ Advisor









Date: 26/01/2026
