| Summary |  |
| --- | --- |
| Application Details |  |
| Permit Number | CG0013501 |
| Application Reference | PAN-032314 |
| Submission Batch | AMP8 WFD PD IMP (30/03/2026) |
| NEP Driver | W_WFD_PD_IMP |
| Unique NEP ID | DCWW101648a |
| Operator Name | Dŵr Cymru Cyfyngedig |
| Site/Asset Name | Llithfaen Wastewater Treatment Works |
| Environment Team | Dwyfor a Meirionnydd |
| Area | North West |
| Local Authority | Gwynedd Council |
| Allocated permitting officer | Emma Dulson |

| Dates |  |
| --- | --- |
| Arrived to Permit Delivery Team | 30/03/2026 |
| Payment / added to AMP tracker | 30/03/2026 |
| Arrived with Permit Officer | 30/03/2026 |
| Duly Made Decision | 13/04/2026 |
| Duly Made Notification Sent | 13/04/2026 |
| RFI Sent | 02/04/2026 |

| Administrative Checks |  |  |  |
| --- | --- | --- | --- |
| Correct submission spreadsheet used |  |  | N/A |
| Correct variation type and fee |  |  | YES |
| Variation type: | Normal | Fee: | £2,957 |
| Basic details (site name, address) correct |  |  | YES |
| All documents saved to the DMS |  |  | YES |

| Basic Technical Checks |  |
| --- | --- |
| Correct permit number supplied | YES |
| Relevant NGRs provided and correct | N/A |
| Information provided matches previous permit (e.g. screen size, weir setting, DWF) | N/A |
| Site plan provided and correct | N/A |
| PSKPM provided (if applicable) | N/A |
| Receiving waters correct? | N/A |

| WFD IMPs |  |
| --- | --- |
| Limit changes match the current NEP | NO |

| Only complete the following if the variation is Not Duly Made |  |
| --- | --- |
| Date of Not Duly Made decision | 02/04/2026 |
| Reason for Not Duly Made decision | Submitted limits do not match the NEP - Submitted reduces the TSS to 51 mg/l which matches the NEP, however the NEP also states a reduction of BOD to 34 mg/l and AmmN to 6 mg/l. |
| Deadline for RFI response | 20/04/2026 |

Updated supporting document submitted 10/03/2026 by Claire Grainger.