| Summary |  |
| --- | --- |
| Application Details |  |
| Permit Number | CM0062801 |
| Application Reference | PAN-032797 |
| Submission Batch | AMP8 WFD PD IMP (12/05/2026) |
| NEP Driver | W_WFD_PD_IMP |
| Unique NEP ID | DCWW101674a |
| Operator Name | Dŵr Cymru Cyfyngedig |
| Site/Asset Name | Llanfair Dyffryn Clwyd Wastewater Treatment Works |
| Environment Team | Denbighshire |
| Area | North East |
| Local Authority | Denbighshire County Council |
| Allocated permitting officer | Emma Dulson |

| Dates |  |
| --- | --- |
| Arrived to Permit Delivery Team | 12/05/2026 |
| Payment / added to AMP tracker | 12/05/2026 |
| Arrived with Permit Officer | 13/05/2026 |
| Duly Made Decision | 18/05/2026 |
| Duly Made Notification Sent | 18/05/2026 |

| Administrative Checks |  |  |  |
| --- | --- | --- | --- |
| Correct submission spreadsheet used |  |  | N/A |
| Correct variation type and fee |  |  | YES |
| Variation type: | Normal | Fee: | £3046 |
| Basic details (site name, address) correct |  |  | YES |
| All documents saved to the DMS |  |  | YES |

| Basic Technical Checks |  |
| --- | --- |
| Correct permit number supplied | YES |
| Relevant NGRs provided and correct | N/A |
| Information provided matches previous permit (e.g. screen size, weir setting, DWF) | N/A |
| Site plan provided and correct | N/A - no changes needed |
| PSKPM provided (if applicable) | N/A |
| Receiving waters correct? | YES |

| WFD IMPs |  |
| --- | --- |
| Limit changes match the current NEP | YES |