Medium Combustion Plant Directive Assessment and Annex 1 Information

Prepared for: BioConstruct NewEnergy Ltd

By: ENVIROSOLUTION LTD Suite 53 3a Bridgewater Street Liverpool L1 0AB Date: March 2026

EnviroSolution Ltd

Document Verification

| Site Address | Arrow Bio Waste Recycling Facility Weighbridge Road, Deeside Industrial Park, CH5 2LL |
| --- | --- |
| Report Title | Medium Combustion Plant Directive Assessment and Annex 1 Information |

Disclaimer

This report has been prepared by EnviroSolution Ltd who has exercised such professional skill, care and diligence as may reasonably be expected of a properly qualified and competent consultant experienced in preparing reports of a similar scope.

However, to the extent that the report is based on or relies upon information contained in records, reports or other materials provided to EnviroSolution Ltd, which have not been independently produced or verified, EnviroSolution Ltd, gives no warranty, representation or assurance as to the accuracy or completeness of such information.

Table of Contents

1	Introduction	4

2	MCPD Applicability Assessment	5

2.1	Rated Thermal Input of Each Combustion Plant	5

2.2	Aggregation	5

2.3	New vs Existing Plant	5

3	Annex 1 Information – MCPD	6

3.1	CHP 1 – MTU 16V4000 GS (2G avus 1200e)	6

3.1.1	Exhaust Gas Emissions (CHP 1)	7

3.2	CHP 2 & CHP 3 – MTU 12V4000 GS (2G avus 1600e)	8

3.2.1	Exhaust Gas Emissions (CHP 2 & 3)	8

3.3	Boiler – Viessmann Vitoplex 200	9

3.4	Emergency Generator – German Generator D 250 GX Heavy Duty	9

4	Summary	10

# Introduction

This document has been prepared in response to a query from Natural Resources Wales (NRW) regarding the applicability of the Medium Combustion Plant Directive (MCPD) (Directive (EU) 2015/2193) to the combustion plant proposed at the Arrow Bio Waste Recycling Facility, Deeside Industrial Park.

The MCPD applies to combustion plants with a rated thermal input equal to or greater than 1 MWth and less than 50 MWth. It was transposed into UK law through the Environmental Permitting (England and Wales) (Amendment) Regulations 2018 and applies to both new and existing medium combustion plants.

This assessment considers the following combustion plant at the facility:

- CHP 1: MTU 16V4000 GS (2G avus 1200e) – biomethane fuelled

- CHP 2: MTU 12V4000 GS (2G avus 1600e) – biomethane fuelled

- CHP 3: MTU 12V4000 GS (2G avus 1600e) – biomethane fuelled

- Boiler: Viessmann Vitoplex 200 – natural gas fuel

- Emergency Generator: German Generator D 250 GX Heavy Duty – diesel fuelled

# MCPD Applicability Assessment

## Rated Thermal Input of Each Combustion Plant

The rated thermal input (energy input) for each combustion plant is determined from the manufacturer’s technical datasheets at 100% load:

| Combustion Plant | Rated Thermal Input (kW) | Rated Thermal Input (MWth) | Electrical Output (kWe) | MCPD Applicable? |
| --- | --- | --- | --- | --- |
| CHP 1 – MTU 16V4000 GS | 4,751 | 4.75 | 2,028 | Yes |
| CHP 2 – MTU 12V4000 GS | 3,560 | 3.56 | 1,521 | Yes |
| CHP 3 – MTU 12V4000 GS | 3,560 | 3.56 | 1,521 | Yes |
| Boiler – Viessmann Vitoplex 200 | 1,100 | 1.10 | N/A | Yes |
| Emergency Generator – D 250 GX | ~500 (est.) | ~0.50 | 200 | No – below 1 MWth |

All three CHP units and the boiler have a rated thermal input ≥1 MWth and <50 MWth and are therefore classified as Medium Combustion Plants under the MCPD. The emergency generator has a rated thermal input below 1 MWth and falls outside the MCPD scope, though it may be classified as a Specified Generator under the Environmental Permitting Regulations if it operates for more than 50 hours per year.

## Aggregation

Under Article 4 of the MCPD, where the waste gases of two or more medium combustion plants are discharged through a common stack, the combination is considered as a single medium combustion plant and their rated thermal inputs are added together for the purpose of determining emission limit values.

At the Arrow Bio facility, each CHP unit has its own individual exhaust stack (10 m height) and the boiler has a separate flue. Therefore, aggregation does not apply and each unit is assessed individually against the relevant emission limit values.

## New vs Existing Plant

All combustion plant at the facility will be commissioned as new plant (post-20 December 2018). They are therefore classified as ‘new medium combustion plants’ under the MCPD and must comply with the emission limit values for new plant from the date they are first operated.

# Annex 1 Information – MCPD

The following information is provided in accordance with Annex 1 of Directive (EU) 2015/2193 for each medium combustion plant at the facility:

## CHP 1 – MTU 16V4000 GS (2G avus 1200e)

| Annex 1 Requirement | Information |
| --- | --- |
| (a) Rated thermal input (MW) | 4.751 MWth (energy input at 100% load per ISO 3046) |
| (b) Type of medium combustion plant | Gas engine – Otto-gas engine, lean burn operation with turbocharging |
| (c) Type of fuels used | Biomethane (upgraded biogas from anaerobic digestion of food waste, CH₄ >95 vol.%). |
| (d) Sector of activity (NACE code) | NACE 38.21 – Treatment and disposal of non-hazardous waste |
| (e) Expected number of annual operating hours and average load in use | Maximum 8,760 hours per year (continuous operation); actual operating hours approximately 8,060 per year following planned four-week annual maintenance programme. Expected average load: 75–100%. |
| (f) Where derogation from ELVs claimed under Article 6(3) – name and address of operator | No derogation claimed. |
| Operator name and address | BioConstruct NewEnergy Ltd, 1 Navigator Court, Preston Farm Industrial Estate, Stockton-On-Tees, TS18 3TQ |
| Location (address / grid reference) | Arrow Bio Waste Recycling Facility, Weighbridge Road, Deeside Industrial Park, Deeside, CH5 2LL. NGR: SJ 31114 71232 |
| Date of commissioning | Expected 2025/2026 (new plant) |
| Electrical output (kWe) | 2,028 kWe at 100% load; 1,521 kWe at 75%; 1,014 kWe at 50% |
| Thermal output (kWth) | 2,149 kWth total (engine block/lube oil/1st stage: 1,093 kW; mixture cooler 1st stage: 808 kW; mixture cooler 2nd stage: 145 kW; optional exhaust heat to 120°C: 1,056 kW) |
| Electrical efficiency | 42.7% at 100% load; 42.0% at 75%; 39.8% at 50% |
| Total efficiency | 87.9% at 100% load; 88.3% at 75%; 88.9% at 50% |
| Exhaust gas temperature | 432°C after turbocharger |
| Stack height | 10 m |
| Engine specification | 16-cylinder V-configuration, 1,500 rpm, bore 170 mm, stroke 210 mm, displacement 76.27 dm³, compression ratio 12.5 |

### Exhaust Gas Emissions (CHP 1)

Raw emissions at 100% load (dry, 5% O₂, normalised to 273K and 101.3 kPa):

| Pollutant | Raw Emission (mg/Nm³) | MCPD ELV – New Plant, Other Gas (mg/Nm³) | Compliant? |
| --- | --- | --- | --- |
| NOx (as NO₂) | < 250 | 250* | Yes |
| CO | < 1,000 | N/A** | – |
| HCHO | < 130 | N/A | – |
| SO₂ | Negligible (biogas desulphurised) | 60 | Yes |
| Dust (PM) | Negligible (gaseous fuel) | N/A for gas | – |

* For engines using ‘other gaseous fuels’ (which includes biogas) with rated thermal input 1–5 MWth, the MCPD ELV for NOx for new plant is 250 mg/Nm³ (Table 1, Part 2, Annex II of the MCPD). Note: where biogas is classified as ‘natural gas’ equivalent (CH₄ >95%), lower ELVs of 95 mg/Nm³ may apply — the operator should confirm the fuel classification with NRW.

** CO is not regulated under the MCPD but may be subject to permit-specific conditions set by NRW.

## CHP 2 & CHP 3 – MTU 12V4000 GS (2G avus 1600e)

Both CHP 2 and CHP 3 are identical units. The Annex 1 information is as follows:

| Annex 1 Requirement | Information |
| --- | --- |
| (a) Rated thermal input (MW) | 3.560 MWth (energy input at 100% load per ISO 3046) |
| (b) Type of medium combustion plant | Gas engine – Otto-gas engine, lean burn operation with turbocharging |
| (c) Type of fuels used | Biomethane (upgraded biogas from anaerobic digestion of food waste, CH₄ >95 vol.%). |
| (d) Sector of activity (NACE code) | NACE 38.21 – Treatment and disposal of non-hazardous waste |
| (e) Expected number of annual operating hours and average load in use | Maximum 8,760 hours per year (continuous operation); actual operating hours approximately 8,060 per year following planned four-week annual maintenance programme. Expected average load: 75–100%. |
| (f) Derogation claimed? | No derogation claimed. |
| Operator name and address | BioConstruct NewEnergy Ltd, 1 Navigator Court, Preston Farm Industrial Estate, Stockton-On-Tees, TS18 3TQ |
| Location | Arrow Bio Waste Recycling Facility, Weighbridge Road, Deeside Industrial Park, CH5 2LL. NGR: SJ 31114 71232 |
| Date of commissioning | Expected 2025/2026 (new plant) |
| Electrical output (kWe) | 1,521 kWe at 100% load; 1,140 kWe at 75%; 760 kWe at 50% |
| Thermal output (kWth) | 1,608 kWth total (engine block/lube oil/1st stage: 828 kW; mixture cooler 1st stage: 602 kW; mixture cooler 2nd stage: 116 kW; optional exhaust heat to 120°C: 780 kW) |
| Electrical efficiency | 42.7% at 100% load; 41.8% at 75%; 39.6% at 50% |
| Total efficiency | 87.9% at 100% load; 88.4% at 75%; 87.9% at 50% |
| Exhaust gas temperature | 422°C after turbocharger |
| Stack height | 10 m |
| Engine specification | 12-cylinder V-configuration, 1,500 rpm, bore 170 mm, stroke 210 mm, displacement 57.2 dm³, compression ratio 12.5 |

### Exhaust Gas Emissions (CHP 2 & 3)

| Pollutant | Raw Emission (mg/Nm³) | MCPD ELV – New Plant (mg/Nm³) | Compliant? |
| --- | --- | --- | --- |
| NOx (as NO₂) | < 250 | 250* | Yes |
| CO | < 1,300 | N/A** | – |
| HCHO | < 130 | N/A | – |
| SO₂ | Negligible (biogas desulphurised) | 60 | Yes |
| Dust (PM) | Negligible (gaseous fuel) | N/A for gas | – |

* Same ELV considerations as CHP 1 above.

## Boiler – Viessmann Vitoplex 200

| Annex 1 Requirement | Information |
| --- | --- |
| (a) Rated thermal input (MW) | 1.1 MWth |
| (b) Type of medium combustion plant | Boiler – three-pass low-temperature boiler with modulating water temperature |
| (c) Type of fuels used | Natural gas |
| (d) Sector of activity | NACE 38.21 – Treatment and disposal of non-hazardous waste |
| (e) Expected operating hours and load | Emergency/backup operation only when CHP units are out of service. Expected <500 hours per year. Variable load. |
| (f) Derogation claimed? | No derogation claimed. |
| Operator | BioConstruct NewEnergy Ltd |
| Location | Arrow Bio Waste Recycling Facility, Weighbridge Road, Deeside, CH5 2LL |
| Date of commissioning | Expected 2025/2026 (new plant) |

The boiler at 1.1 MWth falls within the MCPD scope (≥1 MWth). As it operates solely on natural gas, the ‘natural gas’ ELVs under Table 1, Part 1, Annex II of the MCPD apply.

## Emergency Generator – German Generator D 250 GX Heavy Duty

The emergency diesel generator has a rated electrical output of 200 kWe. Based on typical diesel generator efficiency of approximately 35–40%, the estimated rated thermal input is approximately 500–570 kWth (0.5–0.57 MWth). This is below the 1 MWth threshold and therefore the generator does not fall within the scope of the MCPD.

However, the generator should be assessed against the Specified Generator requirements under the Environmental Permitting (England and Wales) Regulations 2018 (as amended). If the generator operates for more than 50 hours per year, it may require permitting as a Specified Generator. Given that this is an emergency-only backup generator, operation is expected to be significantly below 50 hours per year, but the operator should confirm this with NRW and maintain a log of operating hours.

# Summary

| Plant | Thermal Input (MWth) | Fuel | MCPD? | New/Existing | Specified Generator? | Operating Hours/yr |
| --- | --- | --- | --- | --- | --- | --- |
| CHP 1 | 4.75 | Biomethane | Yes | New | N/A | 8,760 |
| CHP 2 | 3.56 | Biomethane | Yes | New | N/A | 8,760 |
| CHP 3 | 3.56 | Biomethane | Yes | New | N/A | 8,760 |
| Boiler | 1.10 | Natural gas | Yes | New | N/A | <500 (est.) |
| Emergency Gen. | ~0.5 | Diesel | No | N/A | To confirm* | <50 (est.) |

* The operator will confirm with NRW whether the emergency generator requires permitting as a Specified Generator and will maintain an operating hours log.

All four medium combustion plants (3x CHP + 1x boiler) are new plant and will comply with the applicable MCPD emission limit values from the date of first operation. The rated thermal inputs have been derived from the manufacturer’s technical datasheets (MTU/Rolls-Royce for the CHP units and Viessmann for the boiler).

Emission monitoring will be carried out in accordance with Article 6 of the MCPD and any conditions specified in the Environmental Permit, including initial monitoring within four months of first operation and subsequent periodic monitoring at intervals specified by NRW.