Margam and Port Talbot Substations and Interconnector

Activity 1:

Surface Water Discharge

Prepared by: Laing O’Rourke

Version: For Information

Revision: P01

Reference: MARPT-LOR-XX-XX-PL-R-090022

Activity 1: Surface Water Discharge

S5 – For review and acceptance

Security Classification: Public

Document Number: MARPT-LOR-XX-XX-PL-R-090022

| Revision | Author | Checked by | Approved by | Date | Reason for revision |
| --- | --- | --- | --- | --- | --- |
| P01 | Rhodri Davies | Matthew Wisdom | Rob Jones | 06/01/2026 | Permit Application |

DOCUMENT OWNER: Rhodri Davies

SECURITY CLASSIFICATION: OFFICIAL

Handling instructions:   Uncontrolled when printed

| Project Watercourse | Margam Substation Upper-Mother-Ditch |
| --- | --- |
| Duration | June 2026-June 2027 (12 Months) |
| Site Office | Margam Substation Cefn Gwrgan Rd SA13 2BZ. W3W - ///applies.hoped.stirs |
| Discharge Location | National Grid Ref – SS 78922 8567 |
| Purpose & Context | This activity covers the temporary collection, treatment and controlled discharge of rainfall‑dependent construction water arising from HDD entry/exit pits and working areas on BOC land (access roads and laydown areas). The works sit within a ditch‑drained wetland setting; therefore surface run‑off from rainfall can accumulate within excavations and low points during construction. No groundwater abstraction is carried out and no measures are undertaken to lower groundwater levels. All flows are intermittent and weather‑dependent and will be discharged under a bespoke NRW Part B6 water‑discharge permit to the Upper Mother Ditch. The HDD system operates as a self‑contained and self‑closing circuit, whereby drilling fluid returns are continuously recovered at the entry pit and routed back into the drilling fluid management system. Fluids are screened, cleaned, and recycled for reuse within the HDD operation. Spent drilling fluids and cuttings are contained within designated pits and tanks, and are removed from site by licensed contractors for appropriate treatment or disposal at authorised facilities. All HDD entry and exit pits are constructed within bunded, sealed working areas designed to prevent any loss of drilling fluids to surrounding land or surface waters. The pits are inspected regularly, and contingency measures are in place to manage any unexpected fluid returns. As a result, no bentonite, drilling slurry, or HDD process water enters the surface water drainage system. |
| Justification | Pumping is required solely to remove rainfall-derived surface water and incidental water accumulation from active HDD working areas to: - maintain safe and stable working conditions; and - prevent uncontrolled silt mobilisation to the ditch network by ensuring that only treated water is discharged. |
| Scope and Location | Effluent type (B6 classification): Trade – rainfall‑dependent construction dewatering/site drainage (no sanitary sewage Source areas: HDD pits and working pads on BOC land only. Receiving water: Upper Mother Ditch (non‑tidal surface water), with the discharge/outfall and monitoring (sample + MCERTS) located adjacent to the HDD working area as shown on the permit plan Duration: construction phase only; permit surrendered on completion. |
| Method | Surface water is guided to sumps within the working area; low‑lift pumps transfer water by short hoses to the treatment unit. Flows are throttled to the unit’s design rate to avoid bypass. |
| Treatment Train | Inlet control/screening to remove gross solids. Coagulation/flocculation – a low‑dose polymer flocculant (construction‑grade, non‑hazardous) may be added proportional to flow to bind fines (silt/peat/clay/bentonite traces). Lamella settlement – flocculated solids settle; sludge is removed to skips/bags for testing and compliant off‑site management or reuse assessment. Polishing & flow control – final filtration (bag/media) prior to a metered outlet to ditch. The final effluent sampling point and MCERTS‑certified flow meter are installed in‑line between the treatment unit and the outfall Maximum instantaneous rate: 17 L/s (treatment capacity 60 m³/h = 16.67 L/s; rounded for compliance Maximum daily volume: 600 m³/day (60 m³/h × 10‑hour pumping allowance) The treatment system is designed to achieve the following final effluent performance, reflecting substances reasonably expected in treated construction water: Suspended Solids (SS): ≤ 30–50 mg/L (project aim ≤ 30 mg/L). Turbidity: typically < 50–100 NTU (operational proxy for SS). pH: 6.5–9.0. |
| Monitoring and compliance | Flow: MCERTS flow meter at outlet; log instantaneous L/s and daily M3 Quality: pH/turbidity at least daily while discharging; SS weekly (increase at start‑up/adverse weather); TPH screen at set‑up/after maintenance or if sheen suspected Upstream/downstream grab samples at agreed frequency to demonstrate no material deterioration of ditch quality Sludge/solids captured in settlement and filters will be containerised (skip/bags) and tested. If suitable under reuse criteria, they may be re‑used on site (e.g., landscaping) or else removed by a licensed contractor to an authorised facility, in line with duty of care and site waste plan |
| Surface Run-off Calculations | Drawings Associated - Site Layout & Dewatering - Surface Run off Calculations |