## Issue Log
Issue and Revision Record
Revision | Date | Originator | Checker | Approver | Description
1 | 2021 | Grace Peel | Shannon Stone | Anita Manns | First submission
2 | 2022 | Grace Peel | Shannon Stone | Anita Manns | Resubmission
3 | 2023-03-15 | Shannon Stone | Anita Manns | Anita Manns | Sch 5 response
4 |  | Amelia Luk | Shannon Stone |  | Resubmission
Document reference: | 100123523_BAT_AFA May 2024
This document is issued for the party which commissioned it and for specific purposes connected with the above-captioned project only. It should not be relied upon by any other party or used for any other purpose.
We accept no responsibility for the consequences of this document being relied upon by any other party, or being used for any other purpose, or containing any error or omission which is due to an error or omission in data supplied to us by other parties.
This document contains confidential information and proprietary intellectual property. It should not be shown to other parties without consent from us and from the party which commissioned it.

## Afan WwTW
BATc number |  | Issue | Description of the techniques in place and how Operator intends to meet each standard | Supporting Evidence (Reference Documents) | Anticipated Compliance Date
[5 empty] | Now | 2025 | 2026+ | N/A
OVERALL ENVIRONMENTAL PERFORMANCE
1 | Environment Management System (EMS) – ALL of the following:
| I. | Management commitment | EN ISO 9001, EN ISO 14001 and EN ISO 55001 | EN(1) 02 Policy Statement | x
| II. | Environmental policy development including CI of performance |  | EN(1) 02 Policy Statement | x
| III. | Planning and implementing procedures & targets in conjunction with financial planning & investment |  | SAMP | x
| IV. | Implementation of procedures
|  | (a) Structure & responsibility | EN ISO 9001, EN ISO 14001 and EN ISO 55001 | IMS(1) 01 Section 24 Roles and Responsibilities. | x
|  | (b) Recruitment, training, awareness & competence |  | IMS(1) 01 Section 13 Training, Awareness and Competence | x
|  | (c) Communication |  | IMS(1) 01 Section 14 Communication. | x
|  | (d) Employee involvement |  | IMS(1) 01 Section 14 Communication. | x
|  | (e) Documentation |  | IMS(1) 01 Section 15 Document Control. | x
|  | (f) Effective process control |  | IMS(1) 01 Section 15 Document Control. | x
|  | (g) Maintenance programmes | EN ISO 9001, EN ISO 14001 and EN ISO 55001. Planned maintenance is carried out in-line with Planned Maintenance Procedures by external Contractors | IMS(1) 01 Section20 Monitoring and Measurement. | x
|  | (h) Emergency preparedness & response | EN ISO 9001, EN ISO 14001 and EN ISO 55001 | IMS(1) 01 Section 18 and 19; Emergency Procedures EP(3) 01-22; | x
|  | (i) Safeguarding compliance with environmental legislation |  | IMS(1) 01 Section 23 and ENF 008 – Environmental Annual Review | x
| V. | Checking performance and taking corrective action
|  | (a) Monitoring & measurement |  | IMS(1) 01 Section 20 | x
|  | (b) Corrective and preventive action |  | IMS(1) 01 Section 21; Corrective Action Procedure SP(2)03 & WO (3) 32 - Level 3 Procedure Permit Notification & Investigation | x
|  | (c) Maintenance of records |  | IMS(1) 01 Section 16, DCWW document control procedure (SP(2)04) and DCWW Document Retention Policy (AM_L_PL1_008). | x
|  | (d) Independent (where practicable) internal or external EMS auditing |  | IMS(1) 01 Section 17 and Business Systems Audit Procedure SP (2) 05 – Level 2 Procedure | x
| VI. | Senior management review of EMS |  | IMS(1) 01 Section 22 Management Review. | x
| VII. | Following development of cleaner technologies |  | DCWW constantly looking at cleaner and emerging technologies and innovative methods for sludge treatment | x
| VIII. | Whole life cycle considerations when designing a new plant i.e. impacts from eventual decommissioning and throughout its operating life |  | SAMP | x
| IX. | Regular sectoral bench marking |  | WaterUK IMS Forum, knowledge sharing. Daily and weekly reports. Comparison of process performance across water sector. | x
| X. | Waste stream management (BAT 2) |  | Biosolids Assurance Scheme | x
| XI. | Inventory of waste water & waste gas streams (BAT 3) |  | See document Welsh Water Permit Application – Response to Natural Resources Wales Schedule 5 notice August 2025 |  |  | X
| XII. | Residues Management Plan – S6.5 | Residue Management Plan - doc ref 100123523_ResidueMP_AFA September 2024 | Residue Management Plan - doc ref 100123523_ResidueMP_AFA September 2024 | X
| XIII. | Accident Management Plan – S6.5 | Accident Management Plan - doc ref 100123523_AMP_AFA September 2024 | Emergency Procedures (100123523_AMP_AFA September 2024) | X
| XIV. | Odour Management Plan (BAT 12) | Odour Management Plan - doc ref 100123523_OdourMP_AFA_September 2024 | 100123523_OdourMP_AFA_September 2024 | X
| XV. | Noise & Vibration Management Plan (BAT 17) | N/A | No specific noise and vibration management plan has been developed and the requirements for this are covered by other procedures. Most likely cause is a complaint or equipment requiring maintenance. However, due to the Site's location and surrounding land activities it is difficult to substantiate a noise complaint to this site. Noise mitigation measures are considered at design stage and look to meet all required legislation. Typical solutions include acoustic enclosures and the utilisation of building are used on some sites, this is reviewed with respect to receptors. During normal operation equipment is routinely check for any increase in noise or vibration, and maintenance jobs raised and carried out where this is the case. Completion of project work is subject to CDM where noise is considered in project execution. Vibration forms a part of equipment testing & maintenance and required to be in line with manufacturers reccomendations. Condition 3.4 Noise of Vibration of permits issued by the [Environment Agency] states that Emissions from the activities shall be free from noise and vibration at levels likely to cause pollution outside the site, as perceived by an authorised officer of the [Regulator] unless the operator has used appropriate measures, including, but not limited to, those specified in any approved noise and vibration management plan to prevent or where that is not practicable to minimise the noise and vibration. The operator shall: (a) if notified by the [Regulator] that the activities are giving rise to pollution outside the site due to noise and vibration, submit to the [Regulator] for approval within the period specified, a noise and vibration management plan which identifies and minimises the risks of pollution from noise and vibration; (b) implement the approved noise and vibration management plan, from the date of approval, unless otherwise agreed in writing by the [Regulator]. |  |  |  | X
2 | Improving overall environmental performance – ALL of the following:
| a. | Set up and implement waste characterisation & pre-acceptance procedures | Source of waste is liquid/sludge delivered to the site by truck from DCWW satellite sites. It is stored in closed odour controlled storage tanks. | Biosolids Assurance Scheme (BAS): 1. Souce Material Risk Assessment & Controls - UK DCWW are committed to undertaking a full sludge characterisation, where considered necessary. Waste acceptance and pre waste acceptanceprocedure provided as doc ref 100123523_WasteAcceptance_AFA September 2024 | x
| b. | Set up and implement waste acceptance procedures |  | BAS: 2. Sludge Treatment; Processes; HACCP & Process Validation Procedures; Biosolids Sampling, Analysis, Parameters & Monitoring - UK. DCWW have a waste acceptance procedure for Domestic Waste Imports (WO(3)19). Waste acceptance and pre waste acceptanceprocedure provided as doc ref 100123523_WasteAcceptance_AFA September 2024 | x
| c. | Set up and implement a waste tracking system & inventory | Our Sludge Logistics govern the feedstocks as part of OfWAT reporting, and have a methodology statement to detail why our monitoring systems are robust, our measurements of feedstocks are detailed and our ISCC accreditation supplements this. | Logger system monitoring and reporting all loads. Backed up with weighbridge procedures and telematics. | x
| d. | Set up and implement an output quality management system | HACCP/BAS compliant with output sampling and analysis. | BAS: 5. Biosolids applications to agricultural land; solid analysis, additions of elements and the Safe Sludge Matrix - UK and Biosolids applications to agricultural land - England and Wales | x
| e. | Ensure waste segregation |  | BAS: 1. Source Material Risk Assessment & Controls - UK - Only one influent i.e. sludge. Delivered as liquid and cake into dedicated facilities. | x
| f. | Ensure waste compatibility prior to mixing or blending |  | BAS: 1. Source Material Risk Assessment & Controls - UK and BAS: 2. Sludge Treatment; Processes; HACCP & Process Validation Procedures; Biosolids Sampling, Analysis, Parameters & Monitoring - UK | x
| g. | Sort solid incoming waste – S6.4 |  | BAS: 1. Source Material Risk Assessment & Controls - UK and BAS: 2. Sludge Treatment; Processes; HACCP & Process Validation Procedures; Biosolids Sampling, Analysis, Parameters & Monitoring - UK. No solid waste accepted. | x
3 | Establish and maintain a waste water and waste gas inventory as part of the EMS - ALL of the following:
Information on characteristics of waste and waste treatment processes
| (i)(a) | simplified process flow sheets showing emission sources | For all of BAT 3 below - largely covered by the site’s environmental plans and statutory maintenance’s remit. Our Sludge Logistics govern the feedstocks as part of OfWAT reporting, and have a methodology statement to detail why our monitoring systems are robust, our measurements of feedstocks are detailed and our ISCC accreditation supplements this. We work with our project colleagues to capture this as part of H1 assessments and project scoping to implement the permits in the first place, but we don’t then do anything further to amend the permits or implement additional monitoring. | A process flow diagram and site layout plan is provided with the permit application. The plan shows all potentially contaminated water is directed to the appropriate discharge point and clearly distinguishes between clean water flows and potentially contaminated water flows.a. A single, simplified process flow diagram that clearly shows, all main stages of the treatment process, all emission sources air, water, and water and how they generated and controlled, and outlets from OCU’s or other abatement systems is presented in drawing ref: B17497-123532-ZZ-ZZ-DI-PA-PR1007 Afan Sch 5 response – PFD 040825. |  | x
| (i)(b) | Process-integrated and waste water/waste gas treatment descriptions including performance |  | Emissions performance documented. | x
Information on characteristics of waste water streams
| (ii)(a) | Mean and variability of:
|  | Flow | Waste water stream = return liquors to the head of the wastewater treatment works | PVSS (m3/day) | X
|  | pH |  | Updates to the progress of the characterisation of the wastewater streams is presented in doc ref Welsh Water Permit Application – Response to Natural Resources Wales Schedule 5 notice August 2025. DCWW are committed to undertaking the sampling and analysis in line with BAT 3. For any sampling and analysis undertaken as part of permit compliance DCWW is committed to ensure that those undertaking the sampling and analysis will be by accredited to MCERTs, or equivalent standards, where possible. These commitments are already provided in the sampling and analysis plan, provided at part of the Afan application submission (doc ref 100123523_SamplingPlan_AFA September 2024) DCWW has submitted a sampling programme in relation to waste water streams. The sampling programme will be designed to fully characterise the waste waters discharged to Afan wastewater treatment works (WwTW) from emission point S1, sampled at monitoring points M1 as identified in the site layout plan (doc ref100123523_SamplingPlan_AFA September 2024) The programme will include, but not be limited to a methodology, for a minimum of one 24-hour flow proportional sample a month, for the emission point, for a period of 12 months. The programme will detail the sampling methods/standards used, in accordance with BAT conclusion 20 of the Waste Treatment BREF and include the NGRs of the sampling point location. The programme will establish the characteristics of the liquid waste water streams and shall include as a minimum for each emission point: • Average values and variability of flow, pH, temperature and conductivity. • Average concentration and load values of all relevant substances and their variability. • Data on bioeliminability. The programme will sample for all relevant substances and will include: • Hydrocarbon oil index (HOI) (mg/l) • Free cyanide (CN- ) (mg/l) • Adsorbable organically bound halogens (AOX) (mg/l) • Metals and metalloids; arsenic (expressed as As), cadmium (expressed as Cd), chromium (expressed as Cr), hexavalent chromium (expressed as Cr(VI)), copper (expressed as Cu), lead (expressed as Pb), nickel (expressed as Ni), mercury (expressed as Hg), zinc (expressed as Zn) (µg/l) DCWW has submitted a high-level sampling plan as part of the application and will follow the relevant guidance, in this case Environment Agency guidance: • Specific substances and priority hazardous substances – Surface water pollution risk for your environmental permit Surface water pollution risk assessment for your environmental permit - GOV.UK (www.gov.uk). • Monitoring discharges to water: guidance on selecting a monitoring approach Monitoring discharges to water: guidance on selecting a monitoring approach - GOV.UK (www.gov.uk)) The monitoring programme will be carried out and the monitoring data submitted in accordance with NRW's written approval. However, this has yet to be fully established at taken forwards due to the characterisation of dewatering (return) liquors discharged into the head of works. The technical challenges of characterising this ‘dirty’ fraction are considerable and we have still to determine which limits of detection can be achieved in the labs. To allow a clearer picture to emerge of what is possible the Environment Agency are proposing a 2-year extension to the IC deadline. Greater detail will be provided in the RPS when it is published. All of the above is subject to the agreement of the National RPS Panel. I anticipate confirmation will be forthcoming in the coming 3 weeks. DCWW are committed to implementing a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. Flows measured, sampled and analysed for BOD, COD, pH, ammonia and suspended solids. DCWW are committed to undertake sampling and analysis in line with BAT3. |  | x
|  | Temperature |  |  |  | x
|  | Conductivity |  |  |  | x
| (ii)(b) | Mean concentration, load and variability of:
|  | Total suspended solids | Centrate and Filtrate sampled daily | ADF 001 | x
|  | COD/TOC |  | Updates to the progress of the characterisation of the wastewater streams is presented in doc ref Welsh Water Permit Application – Response to Natural Resources Wales Schedule 5 notice August 2025. Not currently tested, and therefore the mean and variability is unknown. DCWW are committed to implement a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. DCWW are committed to undertake sampling and analysis in line with BAT3. |  | x
|  | Nitrogen species |  |  |  | x
|  | Phosphorous |  |  |  | x
|  | Metals |  |  |  | x
|  | Priority substances/micropollutants |  |  |  | x
|  | Any other relevant compounds |  |  |  | x
| (ii)© | Bioeliminability data (see BAT 52):
|  | BOD |  | Updates to the progress of the characterisation of the wastewater streams is presented in doc ref Welsh Water Permit Application – Response to Natural Resources Wales Schedule 5 notice August 2025. Not currently tested, and therefore the mean and variability is unknown. DCWW are committed to implement a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. DCWW are committed to undertake sampling and analysis in line with BAT3. |  | x
|  | BOD to COD ratio |  |  |  | x
|  | Zahn-Wellens test |  |  |  | x
|  | Biological inhibition potential |  |  |  | x
Information on characteristics of waste gas streams
| (iii)(a) | Mean and variability of:
|  | Flow |  | Updates to the progress of the characterisation of the waste gas streams is presented in doc ref Welsh Water Permit Application – Response to Natural Resources Wales Schedule 5 notice August 2025. Not currently tested, and therefore the mean and variability is unknown. DCWW are committed to implement a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. DCWW are committed to undertake sampling and analysis in line with BAT3. DCWW confirm that they will characterise emissions from the odour control units in line with BAT 3 to demonstrate if TVOC and HCI are present in the waste gas stream. Where TVOC and HCI are identified as relevant in the waste gas streams then DCWW will continue to monitor these emissions in line with BAT requirements. DCWW undertake sampling and monitoring of some of it’s gas systems as required under the existing permit for Afan (permit EPR/ZP3032KQ). Monitoring is undertaken by ECL. These include monitoring of the: • CHPs • Boilers • Flare ECL have provided their detailed sampling protocols/methodologies presented in document ref: ECL-QFR-100s Detailed Sampling Protocols for reports V8 31/12/24. Testing results can be found in the following reports: P5869 R001 DCWW Afan Boilers CHPs 2024 – A1 CHP1, A2 CHP2, A3 Boiler1, A4 Boiler 2 P5869 R002 DCWW Afan Flare 2024 – A5 Flare P5579 R001 DCWW Afan Aug 2023 – A3 Boiler 1, A4 Boiler 2, A5 Flare P5334 R001 DCWW Afan July 2022 – A1 CHP1, A2 CHP2, A3 Boiler 1, A4 Boiler 2 P5334 R002 DCWW Afan CHPs Dec 2022 – A1 CHP1, A2 CHP2 P5009 R001 DCWW Afan August 2021 – A1 CHP1, A2 CHP2, A3 Boiler 1 A4 Boiler 2 P5009 R002 DCWW Afan Dec 2021 – A4 Boiler 2 DCWW have provided emissions to air results for 2024 in doc ref Afan reporting form 2024. The operational hours of: • CHP1 in 2024 was 891hrs • CHP2 4.870hrs • Flare 1603hrs which is greater that 10% of the time allowed for emergencies (of 878hrs) This is not representative for future flare operation as DCWW have upgraded the biogas clean-up system at site, including addressing some legacy pressure issues with the biogas pipework, meaning. It is, therefore, anticipated that the flare usage will return to well below 10%. DCWW have ample capacity with CHPs and Boilers on site and year-to-date monitoring shows >95% of biogas being utilised in CHPs or Boilers, although DCWW are yet to commissioned external reporting/testing to evidence this. |  | x
|  | temperature |  |  |  | x
| (iii)(b) | Mean concentration, load and variability of relevant substances:
|  | Organic compounds |  |  |  | x
|  | POPs e.g. PCBs |  |  |  | x
Any other relevant compounds
| (iii)(c) | Flammability |  |  |  | x
|  | Lower and Higher Explosive Limits |  |  |  | x
|  | Reactivity |  |  |  | x
| (iii)(d) | Presence of other substances that may affect the gas treatment system or plant safety:
|  | O2 |  | Recorded 'live' on SCADA | x
|  | N2 |  | Updates to the progress of the characterisation of the wastewater streams is presented in doc ref Welsh Water Permit Application – Response to Natural Resources Wales Schedule 5 notice August 2025. Not currently tested, and therefore the mean and variability is unknown. DCWW are committed to implement a monitoring programme to produce an inventory of the waste water streams. It is therefore, considered that this will be added as Improvement Conditions to the permit. DCWW are committed to undertake sampling and analysis in line with BAT3. |  | x
|  | Water vapour |  |  |  | x
|  | Dust |  |  |  | x
4 | Reducing environmental risk associated with waste storage – ALL of the following:
| a. | Optimised storage location | Distance from watercourse? Walls around storage section, drainage all returns to the wastewater treatment works. BAS 3. | Source of waste is indigenous sludge and imported sludge. Solid waste generated as part of the operations is kept inside and kept separately from other wastes. BAS - 3. Biosolids transportation and storage - England and Wales. No hazardous wastes accepted. Residue management plan provided in relation to other waste streams. Doc ref 100123523_ResidueMP_AFA September 2024 | x
| b. | Adequate storage capacity |  |  | x
| c. | Safe storage operation |  |  | x
| d. | Separate area for storage & handling of packaged hazardous waste |  |  | x
5 | Set up and implement procedures to reduce the environmental risk associated with handling and transfer of waste - include following elements:
| Carried out by competent staff |  | Comply as part of the general site operations. | BAS - 3. Biosolids transportation and storage - England and Wales. All DCWW tanker drivers must undergo training as per the driver induction pack (aka Logistics Agency Induction 001). The induction pack consisting of 30 slides must be kept in the cab whilst driving/working at all times and the information enclosed within it must be available available to emergency services. Slide 28 of the induction pack, the provide procedures for the loading from sludge tanker points and discharge to sludge tanker points and are listed as follows: LOADING FROM SLUDGE TANKER POINT 1. Position Tanker so that the hoses can be easily connected from the well point to the lorry and apply the handbrake. 2. Connect hoses from well point to tanker inlet valve, ensuring that the pipes are secure and vent points are closed. 3. Select Suction (Suck) on control panel. 4. Ensure vac/press gauge starts to record a vacuum in the tank. 5. Open valve on sludge tank point if fitted and Inlet valve on Tanker. 6. Observe level on sight glass and close sludge tank point when on full marker as indicated on the sight glass. 7. Open pipe vent at sludge tank point , to allow sludge to vacuum from the hoses. Once drained, close pipe vent, close tanker inlet valve, disconnect hoses and secure outlets with blanking caps. 8. Release vacuum in tank. 9. Close vent valve. DISCHARGE INTO SLUDGE STORAGE TANK 1. Position Tanker so that the hoses can be easily connected from the storage tank to the lorry and apply the handbrake. 2. Connect hoses from Reception tank (Logger if Applicable) to tanker discharge valve, ensuring that the hoses are secure and vent points are closed. 3. Select Pressure (Blow) on control Panel 4. Ensure vac/press gauge starts to record a pressure in the tank. 5. Open valve on sludge tank point via Logger if fitted and Outlet valve on Tanker 6. Observe level on sight glass and once tanker empty, Close Tanker Outlet valve. 7. Turn off tanker pump. 8. Open Tanker Drain Valve to drain and relieve pressure. 9. Disconnect hoses, close Drain valve, secure outlets with blanking caps and hose down any residue or spillages. In addition, the vehicle discharge points are located on an impermeable surface with sealed drainage system (drains to HoW via the SBRs plant and on to the adjacent Eign WwTW). The tankers are DCWW own tankers and only used to transport liquid sludges, therefore, tanker ‘wash-out’ certification is not required. However, tankers are cleane.d by the tanker driver drawing off FE from the FE tank. They then drive to the inlet works and discharges the water from the tanker into the inlet works via a pipe. It is not a frequent occurrence. The inlet works has an impermeable surface, wash down (hose) facility and drains to the head of the works to go through the Wwt process. Also covered in the Accident Management Plan provided. Doc ref 100123523_AMP_AFA September 2024. | x
| Duly documented, validated and verified |  |  |  | x
| Spill prevention, detection and mitigation measures |  |  |  | x
| Take precautions when mixing or blending wastes |  |  |  | x
Procedures are risk-based and consider likelihood of accidents, incidents and their environmental impact
x
MONITORING
6 | Relevant emissions to water: monitor key process parameters at key locations
Key process parameters
| Waste water flow |  |  | Updates to the progress of the characterisation of the waste water streams is presented in doc ref Welsh Water Permit Application – Response to Natural Resources Wales Schedule 5 notice August 2025. Comply as part of the discharge consent/no direct emissions to water from permit area. NA - any discharge waters are returned back to the head of the waste water treatment works for further treatment under NRW permit consent for wastewater treatment. DCWW are committed to undertake monitoring of waste water, in line with the outcome of the sampling and analysis in line with BAT3. | x
pH
Temperature
Conductivity
BOD
Other process parameters
Key monitoring locations
| Pre-treatment inlet and/or outlet |  |  | Comply as part of the discharge consent/no direct emissions to water from permit area. NA - any discharge waters are returned back to the head of the waste water treatment works for further treatment under NRW permit consent for wastewater treatment. DCWW are committed to undertake monitoring of waste water, in line with the outcome of the sampling and analysis in line with BAT3. Updates to the progress of the characterisation of the waste water streams is presented in doc ref Welsh Water Permit Application – Response to Natural Resources Wales Schedule 5 notice August 2025. | x
Final treatment inlet
Discharge point (to the environment)
Other location
7 | Monitoring emissions to water (refer to Table 6.1) |  | No emissions to water |  | x
Monitoring parameters depend on waste treatment process(es) involved
8 | Monitoring emissions to air (refer to Table 6.2) |  | Covered in EPR Permit | Updates to the progress of the characterisation of the waste gas streams and emisins to is presented in doc ref Welsh Water Permit Application – Response to Natural Resources Wales Schedule 5 notice August 2025. These compliance requirements are already set out in the EPR. Monitoring will be in line with BAT 8 for the following parameters - H2S and NH3 (or odour concentration) and we will follow the relevant EN standard as described under BAT 8 for biological treatment of waste. | x
Monitoring parameters depend on waste treatment process(es) involved
9 | Monitoring diffuse emissions of organic compounds to air from processes involving solvents. Use one or a combination of the following:
| a | Measurement – S6.2 descriptions | Not applicable, no burning of solvents |  |  |  |  | x
| b | Emissions factor calculation | [5 empty] | x
| c | Mass balance calculation | [5 empty] | x
10 | Periodically monitor odour emissions where nuisance is expected and/or has been substantiated (monitoring frequency is outlined in BAT 12)
| Use EN standards e.g. 13725 or 16841 | [6 empty] | x
| Use equivalent methods e.g. ISO / national / international monitoring standards |  | BAT is to periodically monitor odour emissions. (The monitoring frequency is determined in the odour management plan (see BAT 12).) | See WWWOE (3) 25 - Odour Control Test Monitoring will be in line relevant EN and regulator required standard. | x
11 | Annual monitoring for:
| - Water, energy and raw materials |  | BAT is to monitor the annual consumption of water, energy and raw materials as well as the annual generation of residues and waste water, with a frequency of at least once per year. | Energy use onsite measured annually and submitted to NRW as annual return. Covered by our annual energy consumption reporting to OFWAT, which requires to report total energy consumption (electricity, gas, heating fuels, transport use) for each regulated area of the business. This data is audited annually by Jacobs before submitting the data to OFWAT. The majority of the energy consumption (all electricity & natural gas use which covers ~90%) is monitored against a budget for each individual facility on a monthly basis. This energy consumption is based on metered data from Automatic Meter Readers and/or invoices from the energy suppliers (Ørsted & Corona). See also Dwr Cymru IMS WO (3) 32 Permit Notification & Investigation. Other reports are provided to the regulator as required. | x
| - Generation of residues and waste water |  |  |  | x
EMISSIONS TO AIR
12 | Set up, implement and review an Odour Management Plan (as part of the site EMS) where nuisance is expected and/or has been substantiated. Include ALL of the following:
| Protocol containing actions and timelines |  | The applicability is restricted to cases where an odour nuisance at sensitive receptors is expected and/or has been substantiated. | Odour Management Plan provided as doc ref 100123523_OdourMP_AFA_September 2024 | x
| Protocol for conducting odour monitoring (BAT 10) |  |  |  | x
| Protocol for response to odour incidents/complaints |  |  |  | x
| Odour prevention and reduction programme |  |  |  | x
13 | Techniques to prevent, or where not practicable reduce odour emissions. Use one or a combination of the following:
| a. | Minimising residence times (open systems only) | [5 empty] | x
| b. | Use chemical treatment (N/A if desired output is hampered) | 7.7 Odour Control in the Works Operation Manual (WOM) A series of odour control units are located around the STC site, together constituting the overall site odour control system. • Sludge - 1 x 2 filters • Biological treatment Distribution Chambers - 2 x 1 filters | Refer to Odour Impact Assessment doc ref DCWW22E_EPR_04_Draft_Afan, Odour Management Plan provided as doc ref 100123523_OdourMP_AFA September 2024, Environmental Risk Assessment doc ref 100123523_ERA_AFA September 2024 | x
| c. | Optimising aerobic treatment – see examples. Refer to BAT 36 for wastes other than water-based liquid waste. | Preventing foaming of digesters |  | x
14 | Techniques to prevent, or where not practicable reduce diffuse emissions to air, in particular of dust, organic compounds and odour. Use one or a combination of the following:
| a. | Minimising potential diffuse emission sources – see examples |  | Such design considerations have not been formally recorded. Diffuse emissions from open storage areas are covered in the Odour Management Plan. Pressure Relief Valves (PRVs) are present on digesters, secondary Digesters, gas pipe work, gas bag, CHP, flare stack, boilers. Pressure release valves (PRV) are present on both primary digesters at high level and the gas holder at a lower level. The digesters and secondary digesters have pressure monitors to monitor gas production rates to prevent excess pressure in storage tanks and vessels. Gas production is monitored by a pressure sensor on these assets which indicates a rise or drop in pressure in an emergency by providing a pre-warning typically at 23mbars and releasing the pressure relief valves typically at 25mbars. PRVs are designed to BS EN ISO 28300:2008 or other recognised standards, if installed earlier, as they would have been installed, and maintained, by a specialist contractor at the time. Use of pressure relief valves is restricted through the use of the CHP engines, and flare if required, at a lower bag volume and pressure. At present, DCWW do not record release events from PRVs as there is no means of recording. When a release has been identified it may be noted in the site diary. SCADA may log a high pressure or a sudden drop in pressure which may indicate the PRV has released. It will not record when the PRV is faulty, although records may be used to identify a report of a PRV fault and action taken. Although long periods of release much be reported to the pollution team and investigation undertaken, but these are more easier to identify by site operatives. | x
| b. | Select and use high-integrity equipment – see examples | Built to standards at time of installation. Applicability may be restricted in the case of existing plants due to operability requirements. | The site was constructed prior to IED, as such we are not able to demonstrate such design considerations were formally considered or recorded. The relevant company standards have been updated to ensure any future projects reflect BAT requirements. The equipment installed at site is considered appropriate for use and in line with industry standards. It is not considered cost effective to replace equipment before end of life and there are no specific plans to replace equipment under this BAT. | x
| c. | Corrosion prevention – see examples | Built to standards at time of installation | All construction and installations are in line with water Industry specifications supplemented with DCWW specifications. | x
| d. | Containment, collection and treatment of diffuse emissions – see examples | All processes contained in tanks or buildings, all emissions collected and emitted through the permitted emissions stack. The use of enclosed equipment or buildings may be restricted by safety considerations such as the risk of explosion or oxygen depletion. The use of enclosed equipment or buildings may also be constrained by the volume of waste. | EN (3) 02 - Waste Management Practice provides some general waste practices and the Odour Management Plan provides measures for management of diffuse odour release, but nothing else formally recorded. IED is considered to have broadened the requirements in relation to this consideration but Afan is anticipated to broadly comply with the BAT. Any gaps will be identified through completion of the air emissions plan through the characterisation of the waste gas streams, which will be provided within 6 months of permit issue. This is part of wider ongoing discussions, specifically with respect to potential bio-aerosol emissions from cake storage, and is considered to require outcomes from initial monitoring (set out in the Bioaerosl risk assessment) to be able to determine appropriate solutions, if required. | x
| e. | Dampening (with water or fog) |  | Not relevant - no significant potential dust sources on site. |  |  |  | x
| f. | Maintenance – see examples | Access available to all equipment | Maintenance access is considered in design in line with CDM requirements. Some changes to equipment are required to meet BAT and this will be included in future design solutions. Where equipment requires specific access arrangements this is to be included in the method statement provided by the contractor completing the work and may require intrinsically safe equipment. Equipment is maintained in line with company requirements and a planned preventative maintenence system is in place for these activities. Annual maintenance schedule with Statutory Maintenance dept. Alarms on PVSS. | x
| g. | Cleaning of waste treatment and storage areas – see examples | General housekeeping | There are general housekeeping and management tasks undertaken and procedures followed by site operatives on a routine basis including WOF 002 Daily/ AGA 2 task sheets. Local wash-water hoses are provided to enable prompt clean up, thus minimising any diffuse odour emissions. | x
| h. | Leak Detection And Repair (LDAR) programme for organics – S6.2 | Leak Detection and Repair Plan see doc ref 100123523_LDAR_AFA September 2024 | Uncontrolled releases of biogas is monitored by pressure instrumentation of the system pressure relief valves, resulting in alarm conditions to warn the site operations team to take corrective action. The Site currently uses SCADA and telemetry monitoring, combined with daily site walkovers with gas monitoring to ensure emissions to air, from leaks are identified and repaired. During routine maintenance a visual walkover surveys for pipework etc is conducted to check for integrity, corrosions and leaks. Leak detection (methane gas analyser) is also installed on biogas holder/s to ensure any leaks from the inner bag are detected. Any leaks detected on the biogas system would always be fixed immediately by DCWW due to the process safety risk of posed by biogas. The use, and potential purchase of Optical gas imagining (OGI) equipment, and subsequent training is being considered by DCWW for use on site to identify emission sources from processes and equipment. A leak detection and repair (LDAR) plan has ben provided, see doc ref 100123523_LDAR_AFA September 2024. Subject to review comments from NRW, it is anticipated that the LDAR will be fullyimplemented by the end of 2027 and then continue as business as usual. The plan acts to improve safety for site operatives, decrease exposure of local sensitive receptors to VOCs, bioaerosols and odour, as well as to reduce product losses. | x
15 | Use flaring only for safety reasons or non-routine operating conditions (OTNOC). Use both of the following:
| a. | Correct plant design – see examples | Wessoes on digesters. Equipment breakdown and excess biogas will result in flaring | Generally applicable to new plants. Biogas produced by the digestion process is re-used on site in Combined Heat and Power (CHP) engine. The electrical output from the CHP engine is used to power the WTW & STC. Where there is a shortfall compared to the site demand this will be met by importing from the grid, where there is a surplus this will be combusted in the waste gas burner (flare). Used for emergency or non-routine activities and recorded on SCADA/PVSS site log for permit compliance. Only run times are monitored against a limit of 10%, above which monitoring is then required to ensure the relevant ELV’s are met. Part of Annual reporting when above 10% of time. Quality of gas being flared is not recorded. Gas generation and use records (doc ref Afan reporting form 2024) shows in 2024, that the site experienced annual flaring of 1603 hours (>10% of time) as identified using SCADA/runtime data on the flare. This is not representative for future operation as DCWW have upgraded the biogas clean-up system at site, including addressing some legacy pressure issues with the biogas pipework, meaning the boilers and CHPs can now run simultaneously on biogas should production levels require. It is, therefore, expected that the flare usage will return to well below 10%. The existing flare will be retained at this site for operation during maintenance or emergency. The CHPs are appropriately sized for the volume of gas produced and it is planned to retain them. With the biogas system having been upgraded in 2024, this means the boilers and CHPs can now run simultaneously on biogas should production levels require. | x
| b. | Plant management including gas system balancing and advanced process control |  | CHP engines and boilers use biogas. The CHP is process controlled through a SCADA system to manage the digestors, gas bag, CHP and Flare together (with associated pumps and valves etc). There is a 2000m3 gas holder in place to provide storage / balancing of biogas feeding into the CHP. In the event the CHP cannot run in an emergency or due to operational issues, biogas will be combusted in the on-site flare stack or it can be utilised in the boiler to allow the treatment process to safely continue effectively and efficiently. Regular servicing carried out. Monitoring will be reviewed to ensure the use of PVRVs is minimised to emergency only (see BAT 14a). | x
16 | Reduce emissions to air when flaring is unavoidable. Use both of the following:
| a. | Correct design of flaring devices – see examples | Built to specifications at time of Implementation. Flare designed to 150% of biogas. In existing plants, applicability may be restricted, e.g. due to maintenance time availability. | The flare is maintained in accordance with manufacturer's specifications and DCWW’s maintenance requirements. Flare stack location and heights are designed based on modelling relevant to the local area, including prevailing weather conditions. The combustion of the biogas by the flare is as efficient as possible and produces a smokeless emission. The flare is used only during emergencies and when the CHP is on downtime for maintenance, although in 2024 Afan had 1 CHP operating due to an alternator failure in September of the previous year. A part had been ordered and a repair commissioned of the failed alternator, however, due to supply chain failures for, and by our contractors, it was May before the alternator was on site. The engine it was attached to then seized so had to be given a rebuild service. The engine that was running throughout this period was getting towards its own scheduled rebuild and was starting to fail, before being rebuilt. In addition, sizable investments in the improvement of the biogas valorisation at Afan were being commissioned with a new inlet plant of chiller, booster and carbon media siloxane filter being brought online to coincide with the return to service of both engines in December. This will now allow Afan to once again fully utilise all throughput in the CHPs. During testing the boilers and CHPs were found to be operating within emission limit values. De-minimis rules did not apply to the flare having operated for more than 10% of the time, as a result of CHP downtime, and as such it was required to be tested, unfortunately it exceeded emission limit values for carbon monoxide. This is not representative for future operation as DCWW have upgraded the biogas clean-up system at site, including addressing some legacy pressure issues with the biogas pipework, meaning. It is, therefore, anticipated that the flare usage will return to below 10%. DCWW have ample capacity with CHPs and Boilers on site and year-to-date monitoring shows >95% of biogas being utilised in CHPs or Boilers, although DCWW are yet to commissioned external reporting/testing to evidence this. Monitoring flare event via flow metre. And report annually as per permit requirements | x
| b. | Monitoring and recording as part of flare management – see examples | We have had H1 assessments undertaken, to document the performance of the waste gas burner and the significance of its emissions when they exceed permit Emissions Limit Values. As a business we have not made funding available to enhance Waste Gas Burner combustion control, from the originally installed specification. We continue to record operating hours and, when greater than 10% of the year, we report as part of our annual permit returns. | Monitoring flare event via flow meter. Report annually as per similar permit requirements for other sites. Flare stack operation is not currently monitored on the Site. Only run times are monitored against a limit of 10%, above which monitoring is then required to ensure the relevant ELV’s are met. Part of Annual reporting when above 10% of time. Quality of gas being flared is not recorded. DCWW undertake sampling and monitoring of some of it’s gas systems as required under the existing permit for Afan (permit EPR/ZP3032KQ). Monitoring is undertaken by ECL. These include monitoring of the: • CHPs • Boilers • Flare ECL have provided their detailed sampling protocols/methodologies presented in document ref: ECL-QFR-100s Detailed Sampling Protocols for reports V8 31/12/24 as part of the Sch 5 response doc Aug 2025. Testing results can be found in the following reports: P5869 R001 DCWW Afan Boilers CHPs 2024 – A1 CHP1, A2 CHP2, A3 Boiler1, A4 Boiler 2 P5869 R002 DCWW Afan Flare 2024 – A5 Flare P5579 R001 DCWW Afan Aug 2023 – A3 Boiler 1, A4 Boiler 2, A5 Flare P5334 R001 DCWW Afan July 2022 – A1 CHP1, A2 CHP2, A3 Boiler 1, A4 Boiler 2 P5334 R002 DCWW Afan CHPs Dec 2022 – A1 CHP1, A2 CHP2 P5009 R001 DCWW Afan August 2021 – A1 CHP1, A2 CHP2, A3 Boiler 1 A4 Boiler 2 P5009 R002 DCWW Afan Dec 2021 – A4 Boiler 2 DCWW have provided emissions to air results for 2024 in doc ref Afan reporting form 2024 as part of the Sch 5 response doc Aug 2025. The operational hours of: • CHP1 in 2024 was 891hrs • CHP2 4.870hrs • Flare 1603hrs which is greater that 10% of the time allowed for emergencies (of 878hrs) Gas generation and use records (doc ref Afan reporting form 2024) show in 2024 that the site experienced annual flaring of 1603 hours (10% of time) as identified using SCADA/runtime data on the flare. This is not representative for future operation as DCWW have upgraded the biogas clean-up system at site, including addressing some legacy pressure issues with the biogas pipework, meaning the boilers and CHPs can now run simultaneously on biogas should production levels require. It is, therefore, expected that the flare usage will return to below 10%. The existing flare will be retained at this site for operation during maintenance or emergency. The CHPs are appropriately sized for the volume of gas produced and it is planned to retain them. With the biogas system having been upgraded in 2024, this means the boilers and CHPs can now run simultaneously on biogas should production levels require. Testing of the flare, in 2024 has shown the flare emissions are not complaint for carbon monoxide. However, given that the biogas upgrade works have been completed, means that the flare usage will reduce to below 10% of operational time and the limits will not require further abatement. Should this be shown, through monitoring of the flare use in 2025, not to be the case DCWW will undertake further work to the flare. Additional work may be required to ensure all BAT requirements are met (e.g. access for testing, the required testing is fully adopted into BAU and related processes, ensure all required signals for data collation and reporting are provided, all specific requirements are met for MCERTs). | x
NOISE AND VIBRATIONS
17 | Set up, implement, and regularly review a Noise and Vibration Management Plan (as part of the EMS) where nuisance is expected and/or has been substantiated. Include ALL of the following:
| I. | Protocol with actions and timelines |  | The applicability is restricted to cases where a noise or vibration nuisance at sensitive receptors is expected and/or has been substantiated. There are currently no protocols in respect of noise and vibration monitoring operating within the business. Noise complaints are investigated and actioned as appropriate. But this is currently not documented. There are currently no protocols in respect of noise and vibration reduction programming operating within the business. Monitoring and investigation are undertaken on an ad hoc basis when the need arises such on receipt of a noise complaint. |  |  |  | x
| II. | Noise and vibration monitoring plan/protocol | But will revisit Noise measurement survey last conducted by Environmental Compliance on 10th May 2016 |  |  |  |  | x
| III. | Noise & vibration complaint response plan/protocol | [5 empty] | x
| IV. | Noise and vibration reduction programme | [5 empty] | x
18 | Techniques to prevent, or where not practicable reduce noise and vibration emissions. Use one or a combination of the following:
| a. | Appropriate location of equipment and buildings | For existing plants, the relocation of equipment and building exits or entrances may be restricted by a lack of space or excessive costs. | A noise and vibration management plan is not considered necessary for the site. These are existing plant and there is no change in the current operations of the site to be permitted under IED. The design of the plant did not need to formally record such design considerations. |  |  |  | x
| b. | Operational measures – see examples |  | Operational procedures for noise and vibration management are dealt with, and actioned, appropriately especially in respect of noise complaints. General site management varies depending on the plant and equipment on site and the techniques employed on the site. All plant and equipment is regularly inspected and maintained to ensure they run effectively and efficiently and are in the best condition they can be to prevent noise and vibration, and staff will raise any maintenance work required. Equipment is only operated and maintained by trained and competent staff, who are familiar with the equipment they are working with and are able to identify when issues arise. The site has restrictions for noisy operations e.g. deliveries, HGV or tanker movements at certain times and there are speed restrictions and speed calming measures in place to help reduce noise. |  |  |  | x
| c. | Low-noise equipment – see examples |  | Where future equipment is to be replaced, low-noise emitting equipment will be considered and new plant and equipment will be required to meet specific standards across all areas (not just noise). |  |  |  | x
| d. | Noise & vibration control equipment – see examples | VA carried out by external contractors | Applicability may be restricted by a lack of space (for existing plants). |  |  |  | x
| e. | Noise attenuation – see examples | Applicable only to existing plants, as the design of new plants should make this technique unnecessary. For existing plants, the insertion of obstacles may be restricted by a lack of space. | Noise attentuation will be installed after careful investigation, appropriateness and consideration of placement. |  |  |  | x
EMISSIONS TO WATER
19 | Optimise water consumption, reduce waste water generation and prevent or where not practicable reduce emissions to soil and water. Use one or a combination of the following:
| a. | Water management – see examples |  | Water usage is one of a number of resources carefully managed to minimise consumption. Where water does not need to be of a potable / clean standard final effluent is used as a 'wash water ' system on all sites. This supply will be used for washing down screens, washing down spills, cleaning tanks, foam suppression and carrier water. | x
| b. | Water recirculation | The Cambi plant does utilise treated final effluent from the adjacent WwTW in preference to potable water. | As mentioned above all STCs recirculate final effluent for washing plant and for a range of non-potable uses. Site drainage directs water landing on impermeable surfaces back to the head of the works to be recirculated through the treatment process. | x
| c. | Impermeable surface |  | All surface water flows are collected in site drainage. Waste treatment area is impermeable with spillages sent to site drainage and ultimately treated at the wastewater treatment works | x
| d. | Reduce likelihood and impact of tank/vessel overflows and failures – see examples |  | Appropriate secondary or tertiary containment measures have been investigated to ensure this BAT is fully implemented and compliant. The presence of high-level detectors and overflow alarms on certain tank units have been installed, where appropriate. Any overflow will drain to the works return system for full treatment through the WwTW. The ADBA assessment doc ref B16399-123532-ZZ-XX-AS-ZA-CI1012 - Afan ADBA Assessment October 2024, the Containment Plan doc ref B16399-123532-ZZ-XX-RP-WA-HY1008 - Afan WwTW Sludge Containment Assessment September 2024 and the Control Philosophy doc ref B16399-123532-XX-AB-MA-ZA-OA0038 - Flood Gates Control Philosophy September 2024 provide the concepts for catastrophic failure. | x
| e. | Roofing of waste storage and treatment areas | Applicability may be constrained when high volumes of waste are stored or treated (e.g. mechanical treatment in shredders of metal waste). | The site has three cake bays (which is covered but not fully enclosed). The bays have an approx. 450m3 total storage capacity. 3 x 70m3 cake storage bays for the temporary storage of cake. The cake will be exported for use as a fertiliser. | x
| f. | Segregation of water streams (being mindful of existing plant constraints) | Generally applicable to new plants. Generally applicable to existing plants within the constraints associated with the layout of the water collection system. | Where there is minimal risk of contamination of surface water e.g. roof water these areas are drained direct to the surface water system and soakaways outside the ccontainment bund. For areas subject to contamination these areas drain to the works return system for full treatment through the WTW. Raw water, final effluent, high quality process water and potable are segregated to avoid inappropriate contamination (Compliance with Water Byelaws). A reviewed and updated the drainage plan (doc ref B14411-123532-XX-XX-DR-CA-CI9005 Afan Sch 5 response - drainage plan Qu 3 290725) has been provided as part of the Sch 5 response. | x
| g. | Adequate drainage infrastructure | Generally applicable to new plants. Generally applicable to existing plants within the constraints associated with the layout of the water drainage system. | Where there is minimal risk of contamination of surface water e.g. roof water these areas are drained direct to the surface water system and soakaways outside the ccontainment bund. For areas subject to contamination these areas drain to the works return system for full treatment through the WTW. Foul/Process drainage segregated from surface water drainage. Site Surface Water Drainage Discharge isolation valve remotely operated in case of major spillage. Water tested and transferred to treatment. A reviewed and updated the drainage plan (doc ref B14411-123532-XX-XX-DR-CA-CI9005 Afan Sch 5 response - drainage plan Qu 3 290725) has been provided as part of the Sch 5 response. | x
| h. | Design and maintenance provisions to allow risk-based leak detection and repair. Minimise use of underground components. | The use of above-ground components is generally applicable to new plants. It may be limited however by the risk of freezing. The installation of secondary containment may be limited in the case of existing plants. | A large proportion of interunit pipework is below ground and leakages are difficult to detect. New pipework is above ground, where possible, and, therefore, any leakages would be visible. Specific areas have been subject to a risk assessment to understand what equipment requires additional containment. | x
| i. | Appropriate buffer storage capacity (being mindful of existing plant constraints) | Appropriate buffer storage capacity is provided for waste water generated during other than normal operating conditions using a risk-based approach (e.g. taking into account the nature of the pollutants, the effects of downstream waste water treatment, and the receiving environment). The discharge of waste water from this buffer storage is only possible after appropriate measures are taken (e.g. monitor, treat, reuse). | Appropriate secondary or tertiary containment measures have been investigated to ensure this BAT is fully implemented and compliant. DCWW will provide a wastewater and digestate buffer storage plan (listed in regard to BAT 4). The Plan’s purpose is to review, desrcibe and propose site contingency arrangements, and to provide, if necessary, appropriate storage capacity or other appropriate measures to prevent or minimise emissions of wastewater or digestate being discharged off site during any occasions when the receiving wastewater treatment works is in storm overflow operating conditions. It is understood the Plan, if required, will need to include, but not be limited to: *Proposals for additional storage capacity, where necessary, with secondary containment within the site boundary for wastewater and/or other digestate during any occasions when the receiving wastewater treatment works is in storm overflow operating conditions. *Procedures to cease discharges during these conditions. *Calculation of a reasonable contingency capacity of waste water and/or other digestate during any occasions when the receiving wastewater treatment works is in storm overflow operating conditions. *A description and design specification of the buffer storage infrastructure and secondary containment measures. The design shall be completed by an appropriately qualified engineer and secondary containment shall be designed in line with CIRIA C736. *A program of works with timescales for the implementation and construction of the buffer storage. *A preventative maintenance and inspection regime. | x
20 | 20183:265F178183:199F178183:199F178183:199F178183:199F178183:199F178183:199F17818183:199
Preliminary, primary and general treatment
| a. | Equalisation |  | Effluent transferred to adjacent treatment works. |  |  |  | x
| b. | Neutralisation | [5 empty] | x
| c. | Physical separation | This happens at the WwTW inlet screens, macerator and grit removal plant |  | x
Physico-chemical treatment
| d. | Adsorption | None of this is required for a coastal discharge from a WwTW regulated under UWWTR | Effluent transferred to adjacent treatment works. |  |  |  | x
| e. | Distillation/rectification | [5 empty] | x
| f. | Precipitation | [5 empty] | x
| g. | Chemical oxidation | [5 empty] | x
| h. | Chemical reduction | [5 empty] | x
| i. | Evaporation | [5 empty] | x
| j. | Ion exchange | [5 empty] | x
| k. | Stripping | [5 empty] | x
Biological treatment
| l. | Activated sludge process |  | Effluent transferred to adjacent treatment works. |  |  |  | x
| m. | Membrane bioreactor |  |  | x
Nitrogen removal
| n. |  |  | Effluent transferred to adjacent treatment works. |  |  |  | x
Solids removal
| o. | Coagulation and flocculation |  | Effluent transferred to adjacent treatment works. |  |  |  | x
| p. | Sedimentation | [5 empty] | x
| q. | Filtration (sand, micro, ultra) | [5 empty] | x
| r. | Flotation | [5 empty] | x
BAT-AELs for DIRECT discharges to a receiving waterbody (mg/l)
Table 6.1 and its supporting notes. Monitoring requirements are outlined in BAT 7
| TOC | 10.0-60 |  | No direct discharges to water. Each site has its own permitted determinands. Typically they will all include BOD, COD, suspended solids, with certain sites having: Iron Phosphorous Total Nitrogen Ammonia The majority of the listed parameters in Table 6.1 of BAT 20 are not monitored. Refer to each site's discharge permits for more details of the site's specific determinands. |  |  |  | x
10-100 for water-based liquid waste
| COD (TOC is preferred) | 30-180 | [5 empty] | x
30-300 for water-based liquid waste
| Suspended solids | 5.0-60 | [5 empty] | x
| HOI | 0.5-10 applying to specific waste treatments | [5 empty] | x
| Total N | 1-25 for biological treatment and waste oil re-refining | [5 empty] | x
10-60 for water-based liquid waste
| Total P | 0.3-2 for biological treatment | [5 empty] | x
1-3 for water-based liquid waste
| Phenol | 0.05-0.2 for waste oil re-refining and physio-chemical treatment of waste with CV | [5 empty] | x
0.05-0.3 for water-based liquid waste
| Free CN- | 0.02-0.1 for water-based liquid waste | [5 empty] | x
| AOX | 0.2-1 for water-based liquid waste | [5 empty] | x
Metals & Metalloids – specific waste treatments as listed in Table 6.1
| As | 0.01-0.05 |  | No direct discharges to water |  |  |  | x
| Cd | 0.01-0.05 | [5 empty] | x
| Cr | 0.01-0.15 | [5 empty] | x
| Cu | 0.05-0.5 | [5 empty] | x
| Pb | 0.05-0.1 | [5 empty] | x
| Ni | 0.05-0.5 | [5 empty] | x
| Hg | 0.5-5 | [5 empty] | x
| Zn | 0.1-1 | [5 empty] | x
Metals & Metalloids – treatment of water-based liquid waste
| As | 0.01-0.1 |  | No direct discharges to water |  |  |  | x
| Cd | 0.01-0.1 | [5 empty] | x
| Cr | 0.01-0.3 | [5 empty] | x
| Hexavalent Cr [Cr(VI] | 0.01-0.1 | [5 empty] | x
| Cu | 0.05-0.5 | [5 empty] | x
| Pb | 0.05-0.3 | [5 empty] | x
| Ni | 0.05-1 | [5 empty] | x
| Hg | 1.0-10 | [5 empty] | x
| Zn | 0.1-2 | [5 empty] | x
BAT-AELs for INDIRECT discharges to a receiving waterbody (mg/l)
Table 6.2 and its supporting notes. Monitoring requirements are outlined in BAT 7
| HOI | 0.5-10 applying to specific waste treatments |  | It is accepted that testing is not currently completed to BAT requirements. DCWW are developing a wastewater sampling plan and this will be provided within 6 months of permit issue. DCWW will look to implement the plan within 12 months of plan agreement but caution that some more complex elements may take longer, due to lab constraints. However, this has yet to be fully established or taken forwards due to the characterisation of dewatering (return) liquors discharged into the head of works. The technical challenges of characterising this ‘dirty’ fraction are considerable and we have still to determine which limits of detection can be achieved in the laboratories. This has been an industry-wide challenge and Water and Sewerage Companies (WaSCs) have engaged with 5five labs on this (ALS, Socotec, Envirolab, RPS and i2) to varying degrees. The issues are summarised as follows: • Deciding an analytical matrix at a lab - sSome laboratories recommend a ‘sludge liquid’ matrix, others a ‘treated sewage effluent’ matrix. • Solids content – laboratories are geared up for analysing samples (that are not Total Suspended Solids) where the solids are below 1%. Return liquors from WwTW AD plants are generally above this. Samplers are having to filter samples on site and over 40% of samples are still being returned as too ‘dirty’. • Ability of labs to analyse the full suite of dets – only 1 laboratory can do all 172 determinantss • Limit of Detection (LoD) – laboratories can report 80 – 90% of determinants at an LOD:EQS sensitivity of less 10% • UKAS accreditation of analysis - Iit is possible to undertake analysis of all 172 determinants across the five5 laboratories, but with a total of only 78 determinants (45%) can be analysed utilising UKAS accredited methods. This leaves 55% (94 determinants) which cannot be analysed with UKAS accredited methods. To enableallow a clearer picture to emerge of what is possible, the Environment Agency are proposing a 2-year extension to the IC deadline set out in the IED permits it has issued. Greater detail will be provided in the Regulatory Position Statement (RPS) when it is published. (This was confirmed via email dated 14/08/2025 from Clive Humphries of the Environment Agency and forwarded to Julie Tate and Jennifer McGuire (NRW)). All of the above is subject to the agreement of the National RPS Panel. Clive Humphries anticipates confirmation will be forthcoming in the coming 3 weeks. DCWW is actively working with other WaSCs through the Water UK Waste and Recycling Network (WRN). |  |  | x
| Free CN- | 0.02-0.1 for water-based liquid waste |  |  |  |  | x
| AOX | 0.2-1 for water-based liquid waste |  |  |  |  | x
Metals & Metalloids – specific waste treatments as listed in Table 6.2
| As | 0.01-0.05 |  | It is accepted that testing is not currently completed to BAT requirements. DCWW are developing a wastewater sampling plan and this will be provided within 6 months of permit issue. DCWW will look to implement the plan within 12 months of plan agreement but caution that some more complex elements may take longer, due to lab constraints. However, this has yet to be fully established or taken forwards due to the characterisation of dewatering (return) liquors discharged into the head of works. The technical challenges of characterising this ‘dirty’ fraction are considerable and we have still to determine which limits of detection can be achieved in the laboratories. This has been an industry-wide challenge and Water and Sewerage Companies (WaSCs) have engaged with 5five labs on this (ALS, Socotec, Envirolab, RPS and i2) to varying degrees. The issues are summarised as follows: • Deciding an analytical matrix at a lab - sSome laboratories recommend a ‘sludge liquid’ matrix, others a ‘treated sewage effluent’ matrix. • Solids content – laboratories are geared up for analysing samples (that are not Total Suspended Solids) where the solids are below 1%. Return liquors from WwTW AD plants are generally above this. Samplers are having to filter samples on site and over 40% of samples are still being returned as too ‘dirty’. • Ability of labs to analyse the full suite of dets – only 1 laboratory can do all 172 determinantss • Limit of Detection (LoD) – laboratories can report 80 – 90% of determinants at an LOD:EQS sensitivity of less 10% • UKAS accreditation of analysis - Iit is possible to undertake analysis of all 172 determinants across the five laboratories, but with a total of only 78 determinants (45%) can be analysed utilising UKAS accredited methods. This leaves 55% (94 determinants) which cannot be analysed with UKAS accredited methods. To enable a clearer picture to emerge of what is possible, the Environment Agency are proposing a 2-year extension to the IC deadline set out in the IED permits it has issued. Greater detail will be provided in the Regulatory Position Statement (RPS) when it is published. (This was confirmed via email dated 14/08/2025 from Clive Humphries of the Environment Agency and forwarded to Julie Tate and Jennifer McGuire (NRW)). All of the above is subject to the agreement of the National RPS Panel. Clive Humphries anticipates confirmation will be forthcoming in the coming 3 weeks. DCWW is actively working with other WaSCs through the Water UK Waste and Recycling Network (WRN). |  |  | x
| Cd | 0.01-0.05 |  |  |  |  | x
| Cr | 0.01-0.15 |  |  |  |  | x
| Cu | 0.05-0.5 |  |  |  |  | x
| Pb | 0.05-0.1 |  |  |  |  | x
| Ni | 0.05-0.5 |  |  |  |  | x
| Hg | 0.5-5 |  |  |  |  | x
| Zn | 0.1-1 |  |  |  |  | x
Metals & Metalloids – treatment of water-based liquid waste
| As | 0.01-0.1 |  | It is accepted that testing is not currently completed to BAT requirements. DCWW are developing a wastewater sampling plan and this will be provided within 6 months of permit issue. DCWW will look to implement the plan within 12 months of plan agreement but caution that some more complex elements may take longer, due to lab constraints. However, this has yet to be fully established or taken forwards due to the characterisation of dewatering (return) liquors discharged into the head of works. The technical challenges of characterising this ‘dirty’ fraction are considerable and we have still to determine which limits of detection can be achieved in the laboratories. This has been an industry-wide challenge and Water and Sewerage Companies (WaSCs) have engaged with 5five labs on this (ALS, Socotec, Envirolab, RPS and i2) to varying degrees. The issues are summarised as follows: • Deciding an analytical matrix at a lab - sSome laboratories recommend a ‘sludge liquid’ matrix, others a ‘treated sewage effluent’ matrix. • Solids content – laboratories are geared up for analysing samples (that are not Total Suspended Solids) where the solids are below 1%. Return liquors from WwTW AD plants are generally above this. Samplers are having to filter samples on site and over 40% of samples are still being returned as too ‘dirty’. • Ability of labs to analyse the full suite of dets – only 1 laboratory can do all 172 determinantss • Limit of Detection (LoD) – laboratories can report 80 – 90% of determinants at an LOD:EQS sensitivity of less 10% • UKAS accreditation of analysis - Iit is possible to undertake analysis of all 172 determinants across the five laboratories, but with a total of only 78 determinants (45%) can be analysed utilising UKAS accredited methods. This leaves 55% (94 determinants) which cannot be analysed with UKAS accredited methods. To enable a clearer picture to emerge of what is possible, the Environment Agency are proposing a 2-year extension to the IC deadline set out in the IED permits it has issued. Greater detail will be provided in the Regulatory Position Statement (RPS) when it is published. (This was confirmed via email dated 14/08/2025 from Clive Humphries of the Environment Agency and forwarded to Julie Tate and Jennifer McGuire (NRW)). All of the above is subject to the agreement of the National RPS Panel. Clive Humphries anticipates confirmation will be forthcoming in the coming 3 weeks. DCWW is actively working with other WaSCs through the Water UK Waste and Recycling Network (WRN). |  |  | x
| Cd | 0.01-0.1 |  |  |  |  | x
| Cr | 0.01-0.3 |  |  |  |  | x
| Hexavalent Cr [Cr(VI] | 0.01-0.1 |  |  |  |  | x
| Cu | 0.05-0.5 |  |  |  |  | x
| Pb | 0.05-0.3 |  |  |  |  | x
| Ni | 0.05-1 |  |  |  |  | x
| Hg | 1.0-10 |  |  |  |  | x
| Zn | 0.1-2 |  |  |  |  | x
EMISSIONS FROM ACCIDENTS AND INCIDENTS
21 | Techniques to prevent or limit the environmental consequences of accidents and incidents, as part of the Accident Management Plan. Use ALL of the following:
| a. | Protection measures – see examples | Accident Management plan existing, but updated to meet the BAT standard. | Accident Management Plan provided doc ref 100123523_AMP_AFA September 2024 | x
| b. | Management of incidental or accidental emissions |  | Critical Parameters Board WOF008 and IMS(1) 01 Section 18 and 19; Emergency Procedures EP(3) 01-22; Accident Management Plan provided doc ref 100123523_AMP_AFA September 2024 | x
| c. | Incident/accident registration and assessment system – see examples | Toolbox talks | Assure Portal | x
MATERIAL EFFICIENCY
22 | Use materials efficiently by substituting materials with waste e.g. waste acids/alkalis for pH adjustment, fly ashes for binders |  | Use of final effluent in the Cambi plant as opposed to potable water. Dilution water, cooling system & poly make up. Also for site hoses. | The STC uses a by-product of waste water treatment to create biogas which is used to produced heat and power (renewable energy) for the site. Following the digestion process, the digestate is treated (depending requirements) to meet the quality requirement set out in the Safe Sludge Matrix and to comply with the HACCP plan. The treated sludge is recycled to agricultural land. Final effluent produced by the wastewater treatment works will be used on the site wherever possible instead of potable water. Details of waste activities is provided in the Main Supporting Document for the permit application doc ref 100123523_MSD_AFA September 2024 | x
ENERGY EFFICIENCY
23 | Use energy efficiently by using both of the following techniques:
| a. | Energy efficiency plan | Energy efficiency techniques | Annual reviews of energy efficiency, minimum of four yearly Energy Savings Opportunity Scheme audits. Covered by our Welsh Water AMP 7 investment program Energy Plan. This plan isn’t showing an improvement plan at site/facility level, but provides the level of improvement that we are targeting as a company and the metrics used to monitor progress. Our site optimisation team is developing improvement plans for each facility, which is currently ongoing. | x
| b. | Energy balance record | energy consumption and generation | Energy Team report on this daily and with weekly flash reports. As a business we generate equivalent of 20% of our own energy which is generally sold back to the grid. The remaining 80% of electricity brought in is via non-fossil fuel sources. | x
REUSE OF PACKAGING
24 | Maximise the reuse of packaging as part of a Residues Management Plan (see BAT 1 XII.) |  | Minimal amounts of packaging. All sent for recovery in preference to disposal with our current hazardous and non hazardous waste tender contractor. | Residue Management Plan doc ref 100123523_ResidueMP_AFA September 2024
MECHANICAL TREATMENT OF WASTE (GENERAL BAT)
25 | Reduce emissions to air of dust, particulate-bound metals, PCDD/F and dioxin-like PCBs by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Cyclone – see S6.1 | [5 empty] | NA
| b. | Fabric filter – see S6.1 | [5 empty] | NA
| c. | Wet scrubbing – see S6.1 | [5 empty] | NA
| d. | Water injection into the shredder | [5 empty] | NA
BAT-AEL for channelled dust emissions to air from the mechanical treatment of waste (mg/Nm3)
Table 6.3 and its supporting note. Monitoring requirements are outlined in BAT 8
| Dust | 2.0-5.0 | [5 empty] | NA
MECHANICAL TREATMENT OF METAL WASTE BY SHREDDING
26 | Improve overall environmental performance and prevent emissions due to accidents and incidents. Use BAT 14g AND ALL of the following techniques:
| (a) | Detailed inspection procedure for baled waste before shredding | [5 empty] | NA
| (b) | Remove dangerous items from waste inputs and dispose of them in a safe manner | [5 empty] | NA
| (c) | Treatment of containers accompanied by a declaration of cleanliness | [5 empty] | NA
27 | Prevent deflagrations and reduce emissions from deflagrations. Use technique a. AND ONE OR BOTH of techniques b. and c.
| a. | Deflagration management plan with reduction programme, incident review and response protocol | [5 empty] | NA
| b. | Pressure relief dampers | [5 empty] | NA
| c. | Pre-shredding (device) | [5 empty] | NA
28 | Use energy efficiently by keeping the shredder feed stable | [6 empty] | NA
MECHANICAL TREATMENT OF WEEE CONTAINING VFCS AND/OR VHCS
29 | Techniques to prevent, or where not practicable reduce emissions of organic compounds to air. Apply BAT 14d AND BAT14h AND technique a. AND ONE OR BOTH of techniques b. and c.
| a. | Optimised removal and capture of refrigerants and oils | [5 empty] | NA
| b. | Cryogenic condensation | [5 empty] | NA
| c. | Adsorption | [5 empty] | NA
BAT-AELs for channelled TVOC and CFC emissions to air from treatment of WEEE containing VFCs and/or VHCs (mg/Nm3)
Table 6.4. Monitoring requirements are outlined in BAT 8
| TVOC | 3.0-15 | [5 empty] | NA
| CFCs | 0.5-10 | [5 empty] | NA
30 | Prevent emissions due to explosions when treating WEEE containing VFCs and/or VHCs. Use EITHER of the following techniques:
| a. | Inert atmosphere e.g. N2 | [5 empty] | NA
| b. | Forced ventilation | [5 empty] | NA
MECHANICAL TREATMENT OF WASTE WITH CALORIFIC VALUE
31 | Reduce emissions to air of organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1 | [5 empty] | NA
| b. | Biofilter – see S6.1 | [5 empty] | NA
| c. | Thermal oxidation – see S6.1 | [5 empty] | NA
| d. | Wet scrubbing – see S6.1 | [5 empty] | NA
BAT-AEL for channelled TVOC emissions to air from the mechanical treatment of waste with calorific value (mg/Nm3)
Table 6.5 and its supporting note. Monitoring requirements are outlined in BAT 8
| TVOC | 10.0-30.0 | [5 empty] | NA
MECHANICAL TREATMENT OF WEEE CONTAINING MERCURY
32 | Reduce mercury emissions to air by collecting them at source, sending them to abatement and carrying out adequate monitoring. This includes ALL of the following:
| Equipment is enclosed, under negative pressure and connected to a LEV system | [6 empty] | NA
| Waste gas treated using dedusting techniques – see examples – followed by adsorption on activated carbon | [6 empty] | NA
| Monitoring of waste gas treatment efficiency | [6 empty] | NA
| Mercury levels measured at least weekly within treatment and storage areas | [6 empty] | NA
BAT-AEL for channelled mercury (Hg) emissions to air from the mechanical treatment of WEEE containing mercury (µg/Nm3)
Table 6.6. Monitoring requirements are outlined in BAT 8
| Hg | 2.0-7.0 | [5 empty] | NA
BIOLOGICAL TREATMENT OF WASTE (GENERAL BAT)
33 | Reduce odour emissions and improve overall environmental performance by selecting the waste input (to ensure its suitability for biological treatment). See also BAT 2 |  |  | Covered in BAT2 - The waste input is based on the waste codes defined in the permit. Waste inputs to the site and described in more detail in the main supporting document and include in the OMP |  |  |  | x
34 | Reduce emissions to air of dust, organic compounds and odorous compounds (including H2S & NH3) by using one or a combination of the following techniques:
| a. | Adsorption – see S6.1 | Unless otherwise stated, the BAT conclusions presented in Section 3 apply to the biological treatment of waste, and in addition to the general BAT conclusions in Section 1. The BAT conclusions in Section 3 do not apply to the treatment of water-based liquid waste. This mention of wet-scrubbing is not BAT for biogas. We have Siloxane Removal systems at Cardiff. | No abatement technologies used on site. |  |  |  | x
| b. | Biofilter – see S6.1 |  | One of the two OCU units on site use a carbon biofilter, the other is designed to be a wet scrubber, but is currently not operational. OCU 1 is a two-stage odour treatment system comprising a Euro Environment John Cockerill Biomod 6.15 4m biofilter as the first stage and TCA2200 1.4 m carbon filter as the second stage. OCU 1 has design flow of 3,030m3/h. The biofilter is continuously irrigated using final effluent which is recirculated through the media with a partial bleed off to waste. The system is fitted with duty and standby fans which draw air through the biofilter and the push air through the carbon filter. By-pass provisions are in place to enable both stages to be isolated for maintenance. Following treatment, the treated air is discharged through a 2m height stack. The biofilter system removes odorous components from the airstream by a process of absorption and microbial breakdown. The carbon filter then removes residual odorous components by a process of adsorption onto the activated carbon media. DCWW is progressing detailed survey and assessment of the existing OCUs to understand any additional measures that may be required to meet BAT 34 and 53. AWT will inspect the OCUs to determine what work is required and where possible and feasible undetake maintenance activities e.g. replace carbon filter. Olfasense will then undertake a site visit to conduct a quantitative odour impact assessment and will produce an updated report for the STC. Any upgrade or replacement works identified will be developed by MMB to meet the relevant BAT-AELs. All other emissions are in compliance with the limit set out in the Air Quality Assessment (100123523_ERA_ADM2009_AFA). |  |  | x
| c. | Fabric filter – see S6.1. |  | No abatement technologies used on site. |  |  |  | x
| d. | Thermal oxidation – see S6.1 |  | No abatement technologies used on site. |  |  |  | x
| e. | Wet scrubbing – see S6.1 |  | One of the two OCU units on site use a carbon biofilter, the other is designed to be a wet scrubber (OCU2), but is currently not operational. When OCU2 was in use acid (H2SO4) was dosed from a separate acid tank into the reagent sump and then recirculated through the media by spray bars. The system is fitted with duty and standby extract fans which draw air from the sludge belt press building and push it through the scrubber. Duty and standby acid dosing pumps and recalculation pumps are provided. Make up water is supplied by final effluent Bypass provision is provided to enable process maintenance. Modification and reinstatement to operational use of the OCU 2 to BAT requirements will be undertaken as part of the wider IED works on site. DCWW is progressing detailed survey and assessment of the existing OCUs to understand any additional measures that may be required to meet BAT 34 and 53. AWT will inspect the OCUs to determine what work is required and where possible and feasible undetake maintenance activities e.g. replace carbon filter. Olfasense will then undertake a site visit to conduct a quantitative odour impact assessment and will produce an updated report for the STC. Any upgrade or replacement works identified will be developed by MMB to meet the relevant BAT-AELs. All other emissions are in compliance with the limit set out in the Air Quality Assessment (100123523_ERA_ADM2009_AFA). |  |  | x
BAT-AEL for channelled NH3, odour, dust and TVOC emissions to air from the biological treatment of waste (mg/Nm3) (ouE/m3)
Table 6.7 and its supporting notes. Monitoring requirements are outlined in BAT 8
| NH3 | 0.3-20 |  | Monitoring requirements are outlined in the Odour Management Plan doc ref 100123523_OdourMP_AFA September 2024 |  | X
| Odour | 200-1000 |  | Monitoring requirements are outlined in the Odour Management Plan doc ref 100123523_OdourMP_AFA September 2024 |  | X
| Dust | 2.0-5.0 |  | Not applicable as it is not a dusty operation |  |  |  | X
| TVOC | 5.0-40 |  | DCWW confirm that they will characterise emissions from the odour control units in line with BAT 3 to demonstrate if TVOC and HCI are present in the waste gas stream. Where TVOC and HCI are identified as relevant in the waste gas streams then DCWW will continue to monitor these emissions in line with BAT requirements. However, the Environment Agency have confirmed an initial 2 year extension to the IC deadline is proposed for compliance with this TVOC limit, to allow novel technologies to be brought to the market. Compliance with the TVOC limit of 20 mg/m³ as derived from BAT 53, is proving difficult. There have been discussions with wider Water and Sewerage companies (WASCs) about the need to comply with this limit and the regulator have confirmed that compliance will be expected. The Environment Agency are also aware of innovations which offer an opportunity to avoid the widescale deployment of Regenerative Thermal Oxidisers (RTOs). DCWW are anticipating that NRW will agree to follow the same understanding as the Environment Agency. In the meantime, DCWW await the publication of the RPS before confirming what actions it will take in the meantime, as this will have an impact on other sites. |  |  | X
35 | Reduce the generation of waste water and reduce water usage by using ALL of the following:
| a. | Segregation of water streams (see also BAT 19f) | Uncontaminated surface water is segregated. Generally the liquid and solid waste streams of EWC 19 06 05 (liquor) and 19 06 06 (digestate) are not segregated for recovery under SUiAR but can be in the event of breakdown or maintenance. | See BAT 19f Areas of site with the potential for contamination of water (e.g. cake loading area where leachate may be generated) will always drain back to the wastewater treatment works for full treatment, whilst areas that are free from contamination (e.g. roofs, footpaths etc) will drain to the site’s surface water drainage system. | X
| b. | Water recirculation | Final effluent from wastewater treatment process is used for polymer make up, sludge dilution, belt press wash water and sludge cooling system | See BAT 19b Flows on PVSS Final effluent generated by the wastewater treatment works wherever possible instead of potable water is used as a pressure returned effluent as already highlighted in earlier BAT reviews. All wastewater flows from the STC are 'recycled' for full treatment through the WTW. | x
| c. | Minimisation of the generation of leachate | No leachate generation | The final product (digested sludge) is dewatered to at least 25%ds as this is deemed the optimal dry solid percentage - balancing power and poly consumption to achieve this target. |  |  |  | x
BIOLOGICAL TREATMENT OF WASTE: AEROBIC METHODS
36 | Reduce emissions to air and improve overall environmental performance by monitoring and/or controlling key waste and process parameters. Include following elements:
| Waste input characteristics e.g. C to N ratio, particle size | [6 empty] | NA
| Temperature and moisture content within windrows (Moisture monitoring not needed for enclosed processes where H&S issues have been identified) | [6 empty] | NA
| Aeration of the windrow | [6 empty] | NA
| Windrow porosity, height and width | [6 empty] | NA
37 | Reduce diffuse emissions to air of dust, odour and bioaerosols from open-air treatment steps. Use ONE OR BOTH of the following techniques:
| a. | Use of semi-permeable membrane covers | [5 empty] | NA
| b. | Adaptation of operations to the meteorological conditions | [5 empty] | NA
BIOLOGICAL TREATMENT OF WASTE: ANAEROBIC METHODS
38 | Reduce emissions to air and improve overall environmental performance by monitoring and/or controlling key waste and process parameters. Include following elements:
Implement a manual and/or automatic monitoring system to:
| Ensure a stable digester operation |  | Weekly samples and daily monitoring and control of feed | The anaerobic digestion process is fully automated using key process instrumentation (temperature profiles, feed volume and dry solids, pressure, foam level and biogas production and quality) to effectively monitor and optimise key process parameters to ensure stable digester operation. This includes automatic fail-safe systems which will revert the digester into a safe and stable condition in the event of an incident or episode of instability (e.g. If foam levels reach a critical level the digester feed and mixing systems would be inhibited - requiring an operator to reset). Digesters will contain foam detection instrumentation, and anti-foam and chemical dosing systems to suppress foam in the digester headspace. Anti-foam lance and biogas off-take swan-neck pipework arrangement will minimise the risk of foam getting into biogas system and causing issues downstream. The key controls are HACCP control points - RT and temperature - recorded daily and kept within the PVSS system / standard spreadsheet. Other key determinands are also recorded to ensure healthy digestion process. Imports are managed via a production planning process to ensure sites are fed in stable and controlled manner each week. The digesters and auxiliary plant contain instrumentation that will provide early warning of a loss of containment or explosion risk, with appropriate fail-safe operation within the software or hardwired. These include dual-level instrumentation within the digester headspace, as well as level switches in the digester overspill chamber to warn of blockage in the downstream pipework. Digester headspace also contains pressure instrumentation which warns of over pressurisation of the digesters. This is backed up by dual pressure and vacuum relief valves on the digester roof which ventilate to atmosphere. A foam-radar in the digester headspace, combined with an automatic anti-foam dosing system ensures foam does not escape through the biogas off-take pipework, or the PRV's. There is pressure monitoring throughout the biogas system, as well as leak detection on the gas holder and gas detection within buildings to warn of an explosion risk. These systems are linked to fast-acting slam-shut valves which isolate all fuels to combustion plant to remove the risk of a fire or explosion. Digesters and the gas holder are controlled by PRVs, pressure sensors and alarms on whessoe valves. Pressure is monitored through SCADA. | x
| Minimise operational difficulties and associated odour emissions |  | Weekly samples and daily monitoring and control of feed |  | x
| Provide sufficient early warning of system failures |  | All equipment monitored 24hrs a day by the PVSS SCADA system. And alarms attached to relevant equipment |  | x
| Windrow porosity, height and width | [6 empty] | x
Monitoring and/or control of key waste and process parameters – examples below:
| pH and alkalinity of the digester feed |  | za\ | Digester Help Sheet (local document) pH expected range 7.6 to 8.5 Alkalinity expected range 7000 to 10000 | x
| Digester operating temperature |  | Monitored continuously and controlled by a cooling system. With automated features, i.e. if digester temperature is too high, digester feed will stop | PVSS & local Availability sheet The internal temperature of the digesters is approximately 38-40 oC Each digester is fitted with 3No. temperature probes in order to monitor/maintain digester operating temperature. When temperature in the digester is above / below the set‐temperature, more/ less cooling water would need to be passed through the sludge cooler in order to maintain a constant temperature in the digester | x
| Hydraulic and organic loading rates of the digester feed |  | Monitored through flows and sampling | Digester Help Sheet (local document) & PVSS Dry solids expected ranges of 4 to 5.5% Volatile solids expected ranges 55 to 70% | x
| Volatile fatty acids and NH3 concentrations within digester & digestate |  | Sampled weekly | Digester Help Sheet (local document) Volatile fatty acids expected range 1000 to 2000 Ammonia expected range 2500 to 3300 | x
| Biogas quantity, composition (e.g. H2S) and pressure |  | PVSS measures biogas volumes through flow meters. Also measured on CHP engines. Composition measured by handheld gas monitor weekly. Pressure continuously measured on PVSS | Digester Help Sheet (local document) & PVSS Biogas composition ranges: - Methane 58 to 70% - Carbon Dioxide 30 to40% - Oxygen <1% - H2S <100ppm | x
| Liquid and foam levels in the digester |  | Continuously measured on PVSS | PVSS | x
MECHANICAL BIOLOGICAL TREATMENT (MBT) OF WASTE
39 | Reduce emissions to air. Generally applicable to new plants, existing plants may have layout constraints. Use BOTH of the following techniques:
| a. | Segregation of the waste gas streams (refer to inventory described in BAT 3) | [5 empty] | NA
| b. | Recirculation of waste gas. Waste gas treatment is described in BAT 34 and recirculation in BAT 35. | [5 empty] | NA
PHYSICO-CHEMICAL TREATMENT OF SOLID AND/OR PASTY WASTE
40 | Improve overall environmental performance by monitoring the waste input as part of the waste pre-acceptance and acceptance procedures. See also BAT 2.
Monitoring the waste input
| Content of organics, oxidising agents, metals, salts, odorous compounds | [6 empty] | X
| H2 formation potential upon mixing of flue-gas treatment residues/ashes with water | [6 empty] | X
41 | Reduce emissions to air of dust, organic compounds and NH3 by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1 | [5 empty] | X
| b. | Biofilter – see S6.1 | [5 empty] | X
| c. | Fabric filter – see S6.1. | [5 empty] | X
| d. | Wet scrubbing – see S6.1 | [5 empty] | X
BAT-AEL for channelled NH3, odour, dust and TVOC emissions to air from the physico-chemical treatment of solid and/or pasty waste (mg/Nm3)
Table 6.8. Monitoring requirements are outlined in BAT 8
| Dust | 2.0-5.0 | [5 empty] | X
RE-REFINING OF WASTE OIL
42 | Improve overall environmental performance by monitoring the waste input as part of the waste pre-acceptance and acceptance procedures. See also BAT 2.
Monitoring the waste input
| Chlorinated compounds e.g. solvents or PCBs | [6 empty] | NA
43 | Reduce quantity of waste sent for disposal by using ONE OR BOTH of the following techniques:
| a. | Material recovery e.g. organic residues in asphalt products | [5 empty] | NA
| b. | Energy recovery | [5 empty] | NA
44 | Reduce emissions to air of organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1 | [5 empty] | NA
| b. | Thermal oxidation – see S6.1 | [5 empty] | NA
| c. | Wet scrubbing – see S6.1 | [5 empty] | NA
The BAT-AEL for TVOC emissions to air set in Section 4.5 (below) applies.
Monitoring requirements are outlined in BAT 8
PHYSICO-CHEMICAL TREATMENT OF WASTE WITH CALORIFIC VALUE
45 | Reduce emissions to air of organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1 | [5 empty] | X
| b. | Cryogenic condensation – see S6.1 | [5 empty] | X
| c. | Thermal oxidation – see S6.1 | [5 empty] | X
| d. | Wet scrubbing – see S6.1 | [5 empty] | X
The BAT-AEL for TVOC emissions to air set in Section 4.5 (below) applies.
Monitoring requirements are outlined in BAT 8
REGENERATION OF SPENT SOLVENTS
46 | Improve overall environmental performance by using ONE OR BOTH of the following techniques:
| a. | Material recovery (by evaporation from distillation residues) | [5 empty] | NA
| b. | Energy recovery e.g. using distillation residues | [5 empty] | NA
47 | Reduce emissions to air of organic compounds by applying BAT 14d AND using a combination of the following techniques:
| a. | Recirculation of process off-gases in a steam boiler. Avoid generating PCBs and/or PCDD/Fs | [5 empty] | NA
| b. | Adsorption – see S6.1 | [5 empty] | NA
| c. | Thermal oxidation – see S6.1. Avoid generating PCBs and/or PCDD/Fs | [5 empty] | NA
| d. | Condensation or cryogenic condensation | [5 empty] | NA
| e. | Wet scrubbing – see S6.1 | [5 empty] | NA
The BAT-AEL for TVOC emissions to air set in Section 4.5 (below) applies.
Monitoring requirements are outlined in BAT 8
BAT-AEL FOR EMISSIONS OF ORGANIC COMPOUNDS TO AIR – SECTION 4.5
(RE-REFINING OF WASTE OIL)
(PHYSICO-CHEMICAL TREATMENT OF WASTE WITH CV)
(REGENERATION OF SPENT SOLVENTS)
BAT-AEL for channelled TVOC emissions to air from the re-refining of waste oil, physico-chemical treatment of waste with calorific value and regeneration of spent solvents (mg/Nm3)
Table 6.9 and its supporting note. Monitoring requirements are outlined in BAT 8
| TVOC | 5.0-30 | [5 empty] | NA
THERMAL TREATMENT OF SPENT ACTIVATED CARBON, WASTE CATALYSTS AND EXCAVATED CONTAMINATED SOIL
48 | Improve overall environmental performance by using ALL of the following techniques:
| a. | Heat recovery from the furnace off-gas e.g. for preheating combustion air or steam generation | [5 empty] | NA
| b. | Indirectly fired furnace i.e. avoids contact between the furnace contents and the burner flue-gases. Note applicability constraints. | [5 empty] | NA
| c. | Process-integrated techniques to reduce emissions to air – see examples | [5 empty] | NA
49 | Reduce emissions to air of HCl, HF, dust and organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Cyclone – see S6.1 | [5 empty] | NA
| b. | Electrostatic precipitator (ESP) – see S6.1 | [5 empty] | NA
| c. | Fabric filter – see S6.1 | [5 empty] | NA
| d. | Wet scrubbing – see S6.1 | [5 empty] | NA
| e. | Adsorption – see S6.1 | [5 empty] | NA
| f. | Condensation – see S6.1 | [5 empty] | NA
| g. | Thermal oxidation – see S6.1 | [5 empty] | NA
Note supporting text for BAT 49g (thermal oxidation)
Monitoring requirements are outlined in BAT 8. No BAT-AELs have been set for this BATc.
WATER WASHING OF EXCAVATED CONTAMINATED SOIL
50 | Reduce emissions to air of dust and organic compounds from the storage, handling and washing steps by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1 | [5 empty] | NA
| b. | Fabric filter – see S6.1 | [5 empty] | NA
| c. | Wet scrubbing – see S6.1 | [5 empty] | NA
Monitoring requirements are outlined in BAT 8. No BAT-AELs have been set for this BATc.
WATER WASHING OF EXCAVATED CONTAMINATED SOIL
51 | Reduce emissions to air of PCBs and organic compounds and improve overall environmental performance by using ALL of the following techniques:
| a. | Coating of the storage and treatment areas – see examples | [5 empty] | NA
| b. | Implementation of staff access rules to prevent dispersion of contamination – see examples | [5 empty] | NA
| c. | Optimised equipment cleaning and drainage – see examples | [5 empty] | NA
| d. | Control and monitoring of emission to air – see examples | [5 empty] | NA
| e. | Disposal of waste treatment residues – see examples | [5 empty] | NA
| f. | Recovery of solvent when solvent washing is used | [5 empty] | NA
Monitoring requirements are outlined in BAT 8. No BAT-AELs have been set for this BATc.
TREATMENT OF WATER-BASED LIQUID WASTE
52 | Improve overall environmental performance by monitoring the waste input as part of the waste pre-acceptance and acceptance procedures. See also BAT 2.
Monitoring the waste input
| Bio eliminability e.g. BOD, BOD-COD ratio, Zahn-Wellens test, biological inhibition potential |  |  | As per BAT 2 for both sludge import and domestic waste imports |  |  |  | x
| Feasibility of emulsion breaking e.g. lab testing | [6 empty] | x
53 | Reduce emissions to air of HCl, NH3 and organic compounds by applying BAT 14d AND using one or a combination of the following techniques:
| a. | Adsorption – see S6.1 | [5 empty] | x
| b. | Biofilter – see S6.1 |  | As per BAT 14 and 34 - OCU 1 | x
| c. | Thermal oxidation – see S6.1. | [5 empty] | x
| d. | Wet scrubbing – see S6.1 |  | As per BAT 14 and 34 - Wet scrubbing in OCU 2 |  |  |  | x
BAT-AELs for channelled HCl and TVOC emissions to air from the treatment of water-based liquid waste (mg/Nm3)
Table 6.10 and its supporting notes. Monitoring requirements are outlined in BAT 8
| HCl | 1.0-5.0 | [5 empty] | x
| TVOC | 3.0-20 | [5 empty] | x